## trafo_types
name | f_nom | s_nom | v_nom_0 | v_nom_1 | vsc | vscr | pfe | i0 | phase_shift | tap_side | tap_neutral | tap_min | tap_max | tap_step
5kVA 33/0.415 | 50 | 0.005 | 33 | 0.415 | 4 | 1 | 0.08 | 0.24 | 150 | 1 | 0 | -5 | 5 | 2.5
10kVA 33/0.415 | 50 | 0.01 | 33 | 0.415 | 4 | 1 | 0.08 | 0.24 | 150 | 1 | 0 | -5 | 5 | 2.5
15kVA 33/0.415 | 50 | 0.015 | 33 | 0.415 | 4 | 1 | 0.08 | 0.24 | 150 | 1 | 0 | -5 | 5 | 2.5
25kVA 33/0.415 | 50 | 0.025 | 33 | 0.415 | 4 | 1 | 0.1 | 0.24 | 150 | 1 | 0 | -5 | 5 | 2.5
50kVA 33/0.415 | 50 | 0.05 | 33 | 0.415 | 4 | 1 | 0.13 | 0.24 | 150 | 1 | 0 | -5 | 5 | 2.5
100kVA 33/0.415 | 50 | 0.1 | 33 | 0.415 | 4 | 1 | 0.32 | 0.24 | 150 | 1 | 0 | -5 | 5 | 2.5
200kVA 33/0.415 | 50 | 0.2 | 33 | 0.415 | 4 | 1.2 | 0.365 | 0.24 | 150 | 1 | 0 | -5 | 5 | 2.5
315kVA 33/0.415 | 50 | 0.315 | 33 | 0.415 | 4 | 1.325 | 1.05 | 0.2375 | 150 | 1 | 0 | -5 | 5 | 2.5
630kVA 33/0.415 | 50 | 0.63 | 33 | 0.415 | 4 | 1.0794 | 1.18 | 0.1873 | 150 | 1 | 0 | -5 | 5 | 2.5
1000kVA 33/0.415 | 50 | 1 | 33 | 0.415 | 6 | 1.0794 | 1.18 | 0.1873 | 150 | 1 | 0 | -5 | 5 | 2.5
1600kVA 33/0.415 | 50 | 1.6 | 33 | 0.415 | 6 | 1.0625 | 2.2 | 0.13751 | 150 | 1 | 0 | -5 | 5 | 2.5
500kVA 33/0.415 | 50 | 0.5 | 33 | 0.415 | 4 | 1.0794 | 1.18 | 0.1873 | 150 | 1 | 0 | -5 | 5 | 2.5
2000kVA 33/0.415 | 50 | 2 | 33 | 0.415 | 8 | 0.835 | 4 | 0.2 | 150 | 1 | 0 | -5 | 5 | 2.5
2500kVA 33/0.415 | 50 | 2.5 | 33 | 0.415 | 8 | 0.8 | 5 | 0.2 | 150 | 1 | 0 | -5 | 5 | 2.5
4500kVA 33/0.415 | 50 | 4.5 | 33 | 0.415 | 6 | 0.8 | 6 | 0.2 | 150 | 1 | 0 | -5 | 5 | 2.5

## correct points
X | Y | Name | timestamp | begin | end | altitudeMo | tessellate | extrude | visibility | drawOrder | icon | Region | RCC | County | Branch | Constituen | Location | Sub Locati | Substation | Substati_1 |  |  | Internal c | DCS Custom | Date of co | Name_1 | DCS Catego | Design dat | Substati_2 | MV Earthin | LV Earthin | Number of | Contracted | LV Substat | Batch Last | FDB Last U | Last Modif | Approver | Modifying | Graphical | Origin of | Feeder of | Feeder Ele | Feeder Bas | Substati_3 | Number o_1 | Number o_2 | Number o_3 | HT Isolati | Ownership | Cleanup Re | Mounting S | Substati_4 | Earthing | Road/Stree | Physical L | Length Of | Gathered i | Total Maxi | Load Perce | Last Month | Absolute M | Customer R | Validity
36.7606 | -1.3529 | 106600 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Langa'Ta | 106600 | 106600 | 36.7606 | -1.3529 | 300653992 | NO | 01/04/2016 | 32287 - SAIFEE PARK_MAGADI RD. | ( CODE 0 ) - NON-C.W.S. | 01/04/2016 | 315 |  |  | 0 | 0 |  | 30/05/2015 12:37:19 | 01/04/2016 15:57:44 |  |  | 1020_POT_INS | 32287 | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA | OUTDOOR | 0 | 0 | 0 | TAPLINS | KPLC |  | H POLE |  | YES | OFF MAGADI RD | LANGATA | 0 | YES | 0 | 0 |  |  | 121112015023793
36.7555 | -1.3569 | 106612 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Hardy | 106612 | 106612 | 36.7555 | -1.3569 | 300640056 |  | 24/05/2012 | 02037 - KENYA NATIONAL PARK_0 | UNKNOWN |  | 200 |  |  | 0 | 0 |  | 25/05/2015 11:12:25 | 25/05/2015 11:12:26 |  |  | 1020_POT_INS | 2037 | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA |  | 1 | 1 | 0 | FUSES | NONE |  |  |  | YES | MAGADI ROAD | KWS | 0.0447 | YES | 150 | 0
36.7577 | -1.3433 | 12747 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Langa'Ta | 12747 | APOSTLES OF JESUS | 36.7577 | -1.3433 | 300001570 |  | 24/05/2012 | 00458 - KISEMBE ROAD | UNKNOWN |  | 100 |  |  | 0 | 203 |  | 22/08/2014 06:13:30 | 27/08/2015 09:58:58 |  |  | 1020_POT_INS | HRDY EX | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA | OUTDOOR | 59 | 65 | 0 | TAPLINS | KPLC | YES | H POLE | 35 | YES | KISEMBE RD | LANGATA | 3.1001 | NO | 24749 | 3.8 | 551.3 | 3.8
36.7666 | -1.3662 | 13595 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Mugumoini | Bomas | 13595 | BANDA PREPARATORY SCH. | 36.7666 | -1.3662 | 300654000 |  | 24/05/2012 | 16041 - BANDA ROAD_KISEMBE | UNKNOWN |  | 200 |  |  | 0 | 0 |  | 22/08/2014 06:13:30 | 27/08/2015 09:59:26 |  |  | 1020_POT_INS | HRDY EX | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA | OUTDOOR | 42 | 47 | 0 | TAPLINS | KPLC | YES | H POLE | 39 | YES | KISEMBE RD | KISEMBE | 2.562 | NO | 20288 | 0
36.7566 | -1.3695 | 16041 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Hardy | 16041 | BANDA ROAD_KISEMBE | 36.7566 | -1.3695 | 300601468 |  | 24/05/2012 | 14156 - NETWORK INTERNATIONAL | UNKNOWN |  | 200 |  |  | 0 | 6 |  | 08/05/2015 07:25:23 | 27/08/2015 10:04:09 |  |  | 1020_POT_INS | HRDY EX | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA | OUTDOOR | 2 | 2 | 0 | FUSES | KPLC | YES | H POLE |  | YES | magadi road | cambridge | 0.1685 | YES | 113 | 0
36.7576 | -1.3683 | 457 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Hardy | 457 | BANDA ROAD_KISEMBE_II | 36.7576 | -1.3683 | 300001568 |  | 24/05/2012 | 00459 - KISEMBE ESTATE | ( CODE 1 ) - H. V./M.V |  | 100 |  |  | 0 | 149 |  | 22/05/2015 03:25:18 | 20/01/2018 18:24:48 |  |  | 1020_POT_INS | HRDY EX | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA | OUTDOOR | 27 | 32 | 0 | NONE | KPLC |  | H POLE | 49.5 | YES | BANDA SCHOOL | ALONG BANDA SCHOOL EXIT | 2.3477 | YES | 18579 | 0.8 | 109.6 | 0.8 | 121112018010214
36.7616 | -1.3567 | 117295 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Hardy | 117295 | BBROOD KENYA LIMITED | 36.7616 | -1.3567 | 300634591 |  | 24/05/2012 | 16370 - KIKENI DRIVE | UNKNOWN |  | 200 |  |  | 0 | 24 |  | 21/05/2015 02:31:47 | 05/01/2018 11:31:05 |  |  | 1020_POT_INS | KRN HO | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA |  | 49 | 55 | 0 | NONE | KPLC | YES |  | 14.5 | YES | kukeni lane | kukeni close | 2.9068 | YES | 19701 | 0.9 | 264.3 | 1.8
36.7569 | -1.3527 | 04058A |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Langa'Ta | 04058A | BOGANI EAST ROAD_0 | 36.7569 | -1.3527 | 300654004 |  | 24/05/2012 | 32013T - KISEMBE PUMP | UNKNOWN |  | 200 |  |  | 0 | 0 |  | 08/05/2015 07:02:27 | 11/01/2018 09:41:03 |  |  | 1020_POT_INS | HRDY EX | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA |  | 17 | 21 | 0 | TAPLINS | KPLC |  |  |  | YES | MUKOMA ROAD | JUNCTION AT MUKOMA MAGADI ROAD | 1.7616 | YES | 13085 | 0.75 | 213.1 | 1.5
36.7503 | -1.3536 | 13129 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Langa'Ta | 13129 | BOGANI EAST ROAD_I | 36.7503 | -1.3536 | 300002086 |  | 24/05/2012 | 02189 - NDOROBO ROAD | UNKNOWN |  | 100 |  |  | 0 | 25 |  | 13/05/2015 03:22:07 | 05/01/2018 11:28:43 |  |  | 1020_POT_INS | KRN HO | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA |  | 13 | 20 | 0 | NONE | KPLC |  |  |  | YES | mutamayu road | mutamayu road | 1.8089 | YES | 21077 | 0
36.7548 | -1.3531 | 13546 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Langa'Ta | 13546 | BOGANI EAST ROAD_II | 36.7548 | -1.3531 | 300002080 |  | 24/05/2012 | 00446 - PARK VIEW_LANGATA | UNKNOWN |  | 200 |  |  | 0 | 73 |  | 13/05/2015 03:25:28 | 05/01/2018 11:43:16 |  |  | 1020_POT_INS | KRN HO | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA | OUTDOOR | 35 | 39 | 0 | FUSES | KPLC | YES | H POLE |  | YES | AT THE JUNCTION OF NYUMBI ROAD | NYUMBI ROAD JUNCTION | 0.9751 | YES | 11260 | 5.6 | 1616.5 | 11.2
36.7585 | -1.3564 | 00454NR |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Hardy | 00454NR | BOGANI EAST ROAD_III | 36.7585 | -1.3564 | 300002077 |  | 24/05/2012 | 03907 - PARK VIEW EST._LANGATA | ( CODE 0 ) - NON-C.W.S. |  | 200 |  |  | 0 | 531 |  | 28/05/2015 12:41:41 | 05/01/2018 11:44:45 |  |  | 1020_POT_INS | KRN HO | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA | OUTDOOR | 47 | 59 | 0 | TAPLINS | KPLC | YES | H POLE | 96 | YES | nyumbi road | karen giraffe centre | 3.378 | YES | 37728 | 0
36.7531 | -1.3533 | 433 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi | Juja-Nairobi | Nairobi West | Karen | Langata |  |  | 433 | BOGANI EAST ROAD_IV | 36.7531 | -1.3533 | 300002079 |  | 24/05/2012 | 13073 - GATAKA WATER SUPPLY | UNKNOWN |  | 200 |  |  | 0 | 96 |  | 13/05/2015 03:26:41 | 05/01/2018 11:45:48 |  |  | 1020_POT_INS | KRN HO | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA | OUTDOOR | 22 | 26 | 0 | TAPLINS | KPLC | YES | H POLE |  | YES | TUMBILI ROAD | END OF TUMBILI ROAD | 1.5187 | YES | 14591 | 0
36.763 | -1.3505 | 409 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Langa'Ta | 409 | BOGANI ROAD_V | 36.763 | -1.3505 | 300002093 | NO | 24/05/2012 | 02009 - MUNDERENDU RD_LANGATA | ( CODE 0 ) - NON-C.W.S. | 16/05/2016 | 100 |  |  | 0 | 74 |  | 13/05/2015 03:20:45 | 14/06/2018 15:26:08 |  |  | 1020_POT_INS | KRN HO | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA | OUTDOOR | 11 | 16 | 0 | NONE | KPLC |  | H POLE |  | YES | muhuti road | the center for parliamentary | 0.664 | YES | 17028 | 0 |  |  | 121112018061352
36.7654 | -1.346 | 16253 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Langa'Ta | 16253 | BROOKE HOUSE SCHOOL_0 | 36.7654 | -1.346 | 300001556 |  | 24/05/2012 | 00456 - KIPEVU ROAD | ( CODE 0 ) - NON-C.W.S. |  | 100 |  |  | 0 | 279 |  | 08/05/2015 07:06:49 | 04/12/2020 12:25:38 | kpl86749 |  | 1020_POT_INS | HRDY EX | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA | OUTDOOR | 75 | 89 | 0 | TAPLINS | KPLC |  | H POLE |  | YES | zembe road | along sember road | 1.0767 | YES | 36982 |  | 510.6 | 3.5 | 121532020120403 | Legal
36.7633 | -1.3466 | 1956 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Langa'Ta | 1956 | BROOKE HOUSE SCHOOL_I | 36.7633 | -1.3466 | 300704117 |  |  | 106601 - NEAR BROOKHOUSE SCHO | UNKNOWN |  | 200 | [5 empty] | 25/11/2015 04:15:26 | 26/05/2020 15:43:47 | kpl01736 |  |  |  | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA |  | 1 | 1 | [6 empty] | YES | NEAR BROOKHOUSE SCHOOL | NEAR BROOKHOUSE SCHOOL | 0.0472 | YES | 96 | 0
36.7594 | -1.3639 | 04970B |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Hardy | 04970B | BURHANIYA SCHOOL | 36.7594 | -1.3639 | 300745064 |  | 14/11/2017 | 165257 - CATHOLIC UNIVERSITY | ( CODE 2 ) - SUBSTATION |  | 315 | [6 empty] | 30/06/2020 16:24:49 | kpl15804 |  |  |  | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA | OUTDOOR | 1 | 1 |  |  |  |  | H POLE |  | YES |  | CATHOLIC UNIVERSITY | 0.0317 |  | 410
36.7646 | -1.3634 | 169238 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Mugumoini | Bomas | 169238 | CAMBRIDGE | 36.7646 | -1.3634 | 300001526 |  | 24/05/2012 | 04058A - BOGANI EAST ROAD | UNKNOWN |  | 15 |  |  | 0 | 0 |  | 08/05/2015 07:07:31 | 28/03/2014 11:34:09 |  |  | 1020_POT_INS | HRDY EX | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA |  | 40 | 40 | 0 | TAPLINS | KPLC |  | SINGLE POLE |  | YES | BOGANI ROAD | CATHOLIC UNIVERSITY | 0.6829 | YES | 723 | 33.33 | 724.7 | 5
36.7563 | -1.3517 | 4001 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Langa'Ta | 4001 | CATHOLIC UNIVERSITY_0 | 36.7563 | -1.3517 | 300001573 |  | 24/05/2012 | 00457 - BANDA ROAD_KISEMBE_II | UNKNOWN |  | 200 |  |  | 0 | 275 |  | 25/05/2015 10:42:15 | 04/06/2015 12:03:00 |  |  | 1020_POT_INS | HRDY EX | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA |  | 58 | 61 | 0 | TAPLINS | KPLC |  |  | 39 | YES | Banda lane | Sarah Serem house | 2.2916 | YES | 10209 | 1.55 | 442.8 | 3.1
36.7579 | -1.35 | 165257 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata |  |  | 165257 | CATHOLIC UNIVERSITY_I | 36.7579 | -1.35 | 300001514 |  | 24/05/2012 | 00409 - BOGANI ROAD | UNKNOWN |  | 50 |  |  | 0 | 112 |  | 13/05/2015 03:54:56 | 08/06/2015 19:27:46 |  |  | 1020_POT_INS | HRDY EX | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA |  | 22 | 29 | 0 | FUSES | KPLC |  |  | 22.5 | YES | magadi road | hotel troy | 1.1899 | YES | 26055 | 0
36.7563 | -1.3508 | NO.NO.1 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Langa'Ta | NO.NO.1 | CATHOLIC UNIVERSITY_II | 36.7563 | -1.3508 | 300001546 |  | 24/05/2012 | 12105 - PARK PLACE HOTEL | UNKNOWN |  | 200 |  |  | 0 | 471 |  | 08/05/2015 07:24:38 | 28/03/2014 09:35:28 |  |  | 1020_POT_INS | HRDY EX | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA |  | 67 | 69 | 0 | TAPLINS | KPLC |  | H POLE | 60 | YES | magadi road | park place hotel | 1.9581 | YES | 21902 | 0
36.7555 | -1.3571 | 175528 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Hardy | 175528 | CATHOLIC UNIVERSITY OF E A | 36.7555 | -1.3571 | 300001538 |  | 24/05/2012 | 13129 - BOGANI EAST ROAD | UNKNOWN |  | 200 |  |  | 0 | 87 |  | 25/05/2015 10:55:11 | 28/05/2015 19:24:57 |  |  | 1020_POT_INS | HRDY EX | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA |  | 78 | 80 | 0 | TAPLINS | KPLC |  |  |  | YES | Bongani Road | ST. JOHN EUDES CENTRE | 0.7655 | YES | 14261 | 5.5 | 1577.4 | 11
36.7546 | -1.361 | 127138 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Hardy | 127138 | DAWAT 2 | 36.7546 | -1.361 | 300001532 |  | 24/05/2012 | 13546 - BOGANI EAST ROAD | UNKNOWN |  | 315 |  |  | 0 | 36 |  | 08/05/2015 07:01:29 | 28/03/2014 11:29:20 |  |  | 1020_POT_INS | HRDY EX | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA |  | 40 | 44 | 0 | TAPLINS | KPLC |  | H POLE | 64.5 | YES | bogani road | near corat africa | 1.2681 | YES | 16277 | 5.56 | 2515.9 | 17.5
36.7566 | -1.3614 | 45161 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Hardy | 45161 | DAWAT E HADIYA_0 | 36.7566 | -1.3614 | 300001565 |  | 24/05/2012 | 13595 - BANDA PREPARATORY SCH. | UNKNOWN |  | 100 |  |  | 0 | 0 |  | 22/05/2015 03:19:18 | 22/05/2015 15:19:20 |  |  | 1020_POT_INS | HRDY EX | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA |  | 1 | 1 | 0 | TAPLINS | KPLC |  |  | 7.5 | YES | MAGADI ROAD | OUTSIDE BANDA SCHOOL | 0.0332 | YES | 76 | 0
36.761 | -1.3608 | 32027 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Hardy | 32027 | DEWAT E. HADIYA_I | 36.761 | -1.3608 | 300666047 |  | 28/03/2014 | NO.NO.1 - CATHOLIC UNIVERSITY | UNKNOWN |  | 630 |  |  | 0 | 0 |  | 30/05/2015 01:30:27 | 30/05/2015 13:30:28 |  |  | 1020_POT_INS | HRDY EX | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA |  | 1 | 1 | 0 | FUSES | KPLC |  |  |  | YES | INSIDE CATHOLIC UNIVERSITY | INSIDE CATHOLIC UNIVERSITY | 0.0032 | YES | 250 | 0
36.746 | -1.3818 | 168973 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Hardy | 168973 | GATAKA BOREHOLE | 36.746 | -1.3818 | 300666483 |  | 12/03/2007 | 16253 - BROOKE HOUSE SCHOOL | UNKNOWN |  | 315 |  |  | 0 | 3 |  | 08/05/2015 07:05:47 | 17/04/2014 12:29:39 |  |  | 1020_POT_INS | HRDY EX | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA |  | 3 | 3 | 0 | TAPLINS | KPLC |  | H POLE | 42 | YES | ALONG MAGADI ROAD | BROOK HOUSE SCHOOLS | 0.3758 | YES | 271 | 0
36.749 | -1.3815 | 13073 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Hardy | 13073 | GATAKA WATER SUPPLY | 36.749 | -1.3815 | 300002084 |  | 24/05/2012 | 00464 - KISEMBE ESTATE | UNKNOWN |  | 200 |  |  | 0 | 86 |  | 13/05/2015 03:41:56 | 05/01/2018 12:47:00 |  |  | 1020_POT_INS | KRN HO | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA | OUTDOOR | 14 | 16 | 0 | TAPLINS | KPLC |  | H POLE | 33 | YES | mukoma road | mukoma road | 1.2404 | YES | 15033 | 0
36.7471 | -1.3571 | 00453B |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi | Juja-Nairobi | Nairobi West | Karen | Langata |  |  | 00453B | K.B.C._LANGATA | 36.7471 | -1.3571 | 300002099 |  | 24/05/2012 | 00450 - KIKENI ROAD | UNKNOWN |  | 200 |  |  | 1 | 199 |  | 19/05/2015 04:53:49 | 05/01/2018 11:29:50 |  |  | 1020_POT_INS | KRN HO | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA |  | 32 | 42 | 0 | NONE | KPLC |  |  | 14.5 | YES | KIKENNI ROAD | OL LOSOWAN | 2.7697 | YES | 38088 | 24.25 | 6962.1 | 48.5
36.7667 | -1.3805 | 00462B |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Hardy | 00462B | K.C.C.T_MBAGATHI | 36.7667 | -1.3805 | 300663787 |  | 16/12/2013 | 45161 - DAWAT E HADIYA | UNKNOWN |  | 315 | M.V. EARTHING INSTALLATION | M.V. AERIAL EARTH | 0 | 0 | TRANSFORMER 25KVA THREE PHASE 11/.433 K.V. | 22/05/2015 03:22:19 | 05/01/2018 10:59:22 |  |  | 1020_POT_INS | HRDY EX | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA | OUTDOOR | 0 | 0 | 0 | TAPLINS | KPLC | YES | H POLE |  | YES | saife park | saife pzrk | 0.0307 | YES | 0 | 0
36.7733 | -1.3796 | 463 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi | Juja-Nairobi | Nairobi West | Karen | Langata |  |  | 463 | K.W.S_B/HOLE | 36.7733 | -1.3796 | 300001549 |  | 24/05/2012 | 00455 - SAIFEE PARK_MAGADI RD. | ( CODE 0 ) - NON-C.W.S. |  | 315 |  |  | 0 | 508 |  | 22/08/2014 06:13:30 | 06/07/2018 09:05:43 |  |  | 1020_POT_INS | HRDY EX | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA | OUTDOOR | 69 | 70 | 0 | TAPLINS | KPLC | YES | H POLE |  | YES | MAGADI RD | LANGATA | 1.3802 | NO | 4380 | 0.86 | 387.8 | 2.7 | 121112017120409
36.7673 | -1.3638 | 2038 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata |  |  | 2038 | KENYA NATIONAL PARK | 36.7673 | -1.3638 | 300002095 | NO | 24/05/2012 | 01671 - MUHUTI ROAD_LANGATA | ( CODE 0 ) - NON-C.W.S. | 15/02/2016 | 50 |  |  | 0 | 132 |  | 22/08/2014 06:13:30 | 05/01/2018 11:37:21 |  |  | 1020_POT_INS | 1020_POT_INS | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA |  | 28 | 35 | 0 | NONE | KPLC |  |  | 41.5 | YES |  | LANGATA | 2.0451 | NO | 14606 | 7.8 | 554.7 | 3.9
36.7749 | -1.3786 | 2037 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Mugumoini | Bomas | 2037 | KENYA NATIONAL PARK_0 | 36.7749 | -1.3786 | 300652975 |  | 24/05/2012 | 33950 - SIMBA HILL ROAD | UNKNOWN |  | 100 |  |  | 0 | 0 |  | 21/05/2015 12:34:59 | 19/02/2019 12:31:09 | kpl17659m | kpl17659m | 1020_POT_INS | KRN HS | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA | OUTDOOR | 24 | 28 | 0 | TAPLINS | KPLC |  | H POLE | 160 | YES | Simba Hill | outside plot 125 | 1.8664 | YES | 17584 | 0
36.7567 | -1.381 | 16370 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Hardy | 16370 | KIKENI DRIVE | 36.7567 | -1.381 | 300002075 | NO | 24/05/2016 | 00447 - SIMBA HILL ROAD | ( CODE 2 ) - SUBSTATION | 01/04/2016 | 200 | M.V. EARTHING INSTALLATION | L.V. EARTHING INSTALLATION | 0 | 157 |  | 13/05/2015 03:24:17 | 19/02/2019 12:31:10 | kpl17659m | kpl17659m | 1020_POT_INS | KRN HO | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA | OUTDOOR | 55 | 71 | 0 | TAPLINS | KPLC |  | H POLE | 160 | YES | SIMBA HILL ROAD | Corner of the Simba Hill road | 4.0304 | YES | 42220 | 15.9 | 4599.9 | 31.8
36.7568 | -1.3791 | 450 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Hardy | 450 | KIKENI ROAD | 36.7568 | -1.3791 | 300001633 |  | 24/05/2012 | 00463 - K.W.S_B/HOLE | ( CODE 0 ) - NON-C.W.S. |  | 200 |  |  | 0 | 160 |  | 08/05/2015 07:04:51 | 01/10/2020 10:27:16 | kpl17125 |  | 1020_POT_INS | HRDY EX | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA |  | 16 | 18 | 0 | NONE | KPLC |  |  |  | YES | magadi road | inside kws | 0.1517 | YES | 13592 | 2.05 | 592.3 | 4.1 | 121532020093392 | Legal
36.7552 | -1.3632 | 456 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi | Juja-Nairobi | Nairobi West | Karen | Langata | Langa'Ta | Hardy | 456 | KIPEVU ROAD | 36.7552 | -1.3632 | 300001559 |  | 24/05/2012 | 02038 - KENYA NATIONAL PARK | ( CODE 2 ) - SUBSTATION |  | 100 |  |  | 0 | 11 |  | 30/05/2015 10:42:57 | 07/07/2020 15:33:35 | kpl18896 |  | 1020_POT_INS | HRDY EX | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA | OUTDOOR | 15 | 17 | 0 | NONE | KPLC |  | SINGLE POLE |  | YES | 0 | 0 | 0.5613 | YES | 6039 |  |  |  | 121112020011513
36.7505 | -1.3741 | 449 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Hardy | 449 | KISEMBE EAST | 36.7505 | -1.3741 | 300002097 |  | 24/05/2012 | 01670 - MUNDERENDU ROAD_LANGA | UNKNOWN |  | 200 |  |  | 0 | 9 |  | 26/06/2015 03:13:00 | 01/10/2019 08:26:52 | kpl85030 | kpl17659 | 1020_POT_INS | KRN HO | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA | OUTDOOR | 15 | 16 | 0 | TAPLINS | KPLC | YES | H POLE |  | YES | IUCN ROAD | IUCN | 0.9081 | YES | 5078 | 2.1 | 609.2 | 4.2
36.7635 | -1.3679 | 459 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Hardy | 459 | KISEMBE ESTATE_0 | 36.7635 | -1.3679 | 300654035 |  | 24/05/2012 | 00454NR - BOGANI EAST ROAD | UNKNOWN |  | 100 |  |  | 0 | 0 |  | 25/05/2015 09:55:39 | 21/09/2018 16:45:30 |  |  | 1020_POT_INS | HRDY EX | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA |  | 133 | 135 | 0 | TAPLINS | KPLC |  |  |  | YES | Magadi lane/Park place | Nyara. c. centre | 1.3596 | YES | 6950 | 21.4 | 3109.4 | 21.4
36.7624 | -1.3727 | 464 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Hardy | 464 | KISEMBE ESTATE_I | 36.7624 | -1.3727 | 300001640 |  | 24/05/2012 | 00462B - K.C.C.T_MBAGATHI | UNKNOWN |  | 630 |  |  | 0 | 737 |  | 22/08/2014 06:13:30 | 28/03/2014 10:36:59 |  |  | 1020_POT_INS | HRDY EX | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA |  | 61 | 61 | 0 | FUSES | KPLC | YES | GROUND MOUNTED |  | YES | MAGADI RD | ONGATA RONGAI | 1.4892 | NO | 22072 | 2.43 | 2189 | 15.3
36.7682 | -1.372 | 32013T |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Mugumoini | Bomas | 32013T | KISEMBE PUMP_0 | 36.7682 | -1.372 | 300696822 | YES | 23/03/2017 | 127138 - DAWAT 2 | ( CODE 2 ) - SUBSTATION | 26/04/2016 |  | M.V. EARTHING INSTALLATION |  |  |  | L.V. SUBSTATION LEADS FOR 630 KVA GMT 3(2X630)+1(1X630) |  | 26/04/2016 14:22:12 |  |  |  |  | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA | INDOOR | 1 | 1 |  |  |  |  | GROUND MOUNTED |  | YES |  |  | 0.0385 |  | 420 | 0 |  |  | E21112016020074
36.7662 | -1.37 | 460 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Hardy | 460 | KISEMBE PUMP_I | 36.7662 | -1.37 | 300001510 | NO | 24/02/2016 | 01956 - BROOKE HOUSE SCHOOL | ( CODE 0 ) - NON-C.W.S. | 24/02/2016 | 200 |  |  | 0 | 445 |  | 13/05/2015 03:55:47 | 24/02/2016 18:14:04 |  |  | 1020_POT_INS | HRDY EX | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA | OUTDOOR | 5 | 6 | 0 | TAPLINS | KPLC |  | H POLE | 42 | YES | not named | Consolata Shrine | 0.7327 | YES | 6061 | 0 |  |  | 121112015033618
36.7608 | -1.3681 | 458 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Hardy | 458 | KISEMBE ROAD | 36.7608 | -1.3681 | 300706884 |  |  | 106612 - 106612 | ( CODE 2 ) - SUBSTATION |  | 100 | [5 empty] | 25/11/2015 04:18:33 | 24/09/2018 09:41:08 |  |  |  |  | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA |  | 9 | 9 | [6 empty] | YES | unknown | LANGATA | 0.6603 | YES | 94 | 0
36.758 | -1.3421 | langata_tx |  |  |  |  | -1 | 0 | -1 | [9 empty] | langata_tx | langata_tx | 36.758 | -1.3421 | 300002118 |  | 24/05/2012 | 12747 - APOSTLES OF JESUS | ( CODE 2 ) - SUBSTATION |  | 1000 |  |  | 0 | 42 |  | 30/05/2015 12:06:58 | 25/09/2018 13:37:51 |  |  | 1020_POT_INS | HRDY EX | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA | INDOOR | 29 | 29 | 0 | TAPLINS | KPLC |  | GROUND MOUNTED | 1000 | YES | k | before cuea gate b | 0.0168 | YES | 691 | 0
36.7616 | -1.359 | 408 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Hardy | 408 | MAGADI ROAD | 36.7616 | -1.359 | 300002180 |  | 24/05/2012 | 04001 - CATHOLIC UNIVERSITY | UNKNOWN |  | 315 |  |  | 0 | 376 |  | 08/05/2015 07:08:03 | 25/09/2018 13:45:49 |  |  | 1020_POT_INS | HRDY EX | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA |  | 5 | 5 | 0 | FUSES | KPLC |  |  | 315 | YES | LIBRARY ROAD | CATHOLIC UNIVERSITY | 0.8794 | YES | 20 | 0
36.7682 | -1.3763 | 461 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Hardy | 461 | MMU | 36.7682 | -1.3763 | 300748744 |  |  | 168973 - GATAKA BOREHOLE | ( CODE 2 ) - SUBSTATION |  | 0 | [6 empty] | 25/09/2018 15:15:20 |  |  |  |  | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA | OUTDOOR | 3 | 3 |  |  |  |  | H POLE |  | YES |  | GATAKA BOREHOLE | 0.0978 |  | 1050 | 0
36.7635 | -1.3832 | 1671 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Hardy | 1671 | MUHUTI ROAD_LANGATA | 36.7635 | -1.3832 | 300666918 |  | 24/05/2012 | 32027 - DEWAT E. HADIYA | UNKNOWN |  | 315 |  |  | 0 | 0 |  | 19/05/2015 02:41:10 | 01/10/2018 10:56:49 |  |  | 1020_POT_INS | 32027 | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA |  | 76 | 80 | 0 | TAPLINS | KPLC |  |  | 60 | YES | saifee park | saifee park | 0.8221 | YES | 12474 | 0
36.7612 | -1.3796 | 2009 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Hardy | 2009 | MUNDERENDU RD_LANGATA | 36.7612 | -1.3796 | 300002085 |  | 24/05/2012 | 00465 - NDOROBO ROAD | ( CODE 2 ) - SUBSTATION |  | 50 |  |  | 0 | 247 |  | 13/05/2015 03:23:11 | 25/10/2020 15:20:21 | kpl18170 |  | 1020_POT_INS | KRN HO | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA |  | 23 | 25 | 0 | TAPLINS | KPLC |  |  | 7.5 | YES | NDOROBO ROAD | NDOROBO ROAD | 0.8084 | YES | 1851 |  |  |  | 121532020080649 | Legal
36.7645 | -1.3782 | 1670 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Hardy | 1670 | MUNDERENDU ROAD_LANGATA | 36.7645 | -1.3782 | 300001536 | NO | 24/05/2012 | 00433 - BOGANI EAST ROAD | ( CODE 0 ) - NON-C.W.S. | 15/02/2016 | 100 |  |  | 0 | 1230 |  | 25/05/2015 10:07:44 | 29/09/2020 11:15:47 | kpl86749 |  | 1020_POT_INS | HRDY EX | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA |  | 369 | 376 | 0 | FUSES | KPLC |  |  |  | YES | Bongani road | Franciscan Family Association | 0.2606 | YES | 28179 | 45.7 | 6602.5 | 45.7 | 121532020093027 | Legal
36.7603 | -1.3755 | 2189 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Hardy | 2189 | NDOROBO ROAD_0 | 36.7603 | -1.3755 | 300001623 |  | 24/05/2012 | 00460 - KISEMBE PUMP | ( CODE 0 ) - NON-C.W.S. |  | 315 |  |  | 0 | 17 |  | 22/08/2014 06:13:30 | 12/07/2019 11:15:35 | kpl18170 | kpl17659 | 1020_POT_INS | HRDY EX | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA | OUTDOOR | 3 | 3 | 0 | TAPLINS | KPLC | YES | H POLE |  | YES | MAGADI RD | LANGATA | 0.0199 | NO | 1009 | 0 |  |  | 121112018041940
36.7579 | -1.3735 | 465 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi | Juja-Nairobi | Nairobi West | Karen | Langata |  |  | 465 | NDOROBO ROAD_I | 36.7579 | -1.3735 | 300685566 | YES | 09/02/2016 | 117295 - BBROOD KENYA LIMITED | ( CODE 2 ) - SUBSTATION | 09/02/2016 | 200 | M.V. EARTHING INSTALLATION | L.V. EARTHING INSTALLATION |  |  |  |  | 28/01/2019 15:10:46 | kpl17661 | kpl17661 |  |  | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA | OUTDOOR | 1 | 1 |  |  |  |  | H POLE |  | YES |  | BBROOD KENYA LIMITED | 0.014 |  | 150 | 0
36.7587 | -1.38 | 467 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Hardy | 467 | NDOROBO ROAD_II | 36.7587 | -1.38 | 300002091 |  | 24/05/2012 | 00467 - NDOROBO ROAD | UNKNOWN |  | 200 |  |  | 0 | 201 |  | 21/05/2015 12:49:32 | 05/01/2018 11:31:41 |  |  | 1020_POT_INS | KRN HO | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA |  | 24 | 28 | 0 | TAPLINS | KPLC |  |  | 24.5 | YES | munderendu road | mama kali dundas | 2.5565 | YES | 16563 | 0
36.7582 | -1.3758 | 466 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Hardy | 466 | NDOROBO ROAD_III | 36.7582 | -1.3758 | 300002081 |  | 24/05/2012 | 00449 - KISEMBE EAST | UNKNOWN |  | 200 |  |  | 0 | 188 |  | 15/06/2015 03:50:33 | 05/01/2018 11:42:27 |  |  | 1020_POT_INS | KRN HO | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA | OUTDOOR | 16 | 26 | 0 | TAPLINS | KPLC | YES | H POLE | 16 | YES | MUKOMA ROAF | MUKOMA ROAD | 1.9288 | YES | 3687 | 0
36.7621 | -1.3471 | 106601 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata |  |  | 106601 | NEAR BROOKHOUSE SCHOOL | 36.7621 | -1.3471 | 300001628 |  | 24/05/2012 | 00461 - MMU | UNKNOWN |  | 5 |  |  | 0 | 59 |  | 30/05/2015 12:39:14 | 05/01/2018 11:22:48 |  |  | 1020_POT_INS | HRDY EX | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA | OUTDOOR | 4 | 5 | 0 | TAPLINS | KPLC | YES | H POLE | 7.5 | YES | 0 | 0 | 0.2189 | YES | 4003 | 0
36.765 | -1.3636 | 14156 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Mugumoini | Bomas | 14156 | NETWORK INTERNATIONAL | 36.765 | -1.3636 | 300002088 |  | 24/05/2012 | 00466 - NDOROBO ROAD | UNKNOWN |  | 25 |  |  | 0 | 80 |  | 19/05/2015 03:13:36 | 05/01/2018 11:29:13 |  |  | 1020_POT_INS | KRN HO | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA | OUTDOOR | 9 | 11 | 0 | NONE | KPLC | YES | H POLE |  | YES | NDOROBO ROAD | NDOROBO ROAD | 0.3318 | YES | 6039 | 0
36.7699 | -1.38 | node1 |  |  |  |  | -1 | 0 | -1 | [9 empty] | node1 | node1 | 36.7699 | -1.38 | 300001522 |  | 24/05/2012 | 00404 - ST.THOMAS SEMINARY | ( CODE 0 ) - NON-C.W.S. |  | 100 |  |  | 0 | 154 |  | 19/05/2015 03:42:58 | 19/04/2018 15:39:59 |  |  | 1020_POT_INS | HRDY EX | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA | OUTDOOR | 28 | 28 | 0 | FUSES | KPLC |  | H POLE |  | YES | main gate east road | st thomas aquinise semenary | 0.4433 | YES | 7075 | 2.4 | 350.7 | 2.4 | 121112018030805
36.7623 | -1.3607 | node10 |  |  |  |  | -1 | 0 | -1 | [9 empty] | node10 | node10 | 36.7623 | -1.3607 | 300639831 |  | 24/05/2012 | 04970B - BURHANIYA SCHOOL | ( CODE 2 ) - SUBSTATION |  | 1000 |  |  | 0 | 902 |  | 13/05/2015 03:56:47 | 03/10/2018 11:49:02 |  |  | 1020_POT_INS | HRDY EX | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA | INDOOR | 237 | 353 | 0 | FUSES | KPLC |  | GROUND MOUNTED |  | YES | OFF GISEMBE ROAD | SAIFEE PARK | 5.6881 | YES | 150600 | 0.25 | 353.2 | 2.5
36.7625 | -1.3609 | node11 |  |  |  |  | -1 | 0 | -1 | [9 empty] | node11 | node11 | 36.7625 | -1.3609 | 300001541 |  | 24/05/2012 | 00453B - K.B.C._LANGATA | UNKNOWN |  | 315 |  |  | 0 | 417 |  | 24/07/2015 09:06:05 | 25/09/2020 12:21:55 | kpl17659 |  | 1020_POT_INS | HRDY EX | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA | INDOOR | 1 | 1 | 0 | FUSES | KPLC | YES | GROUND MOUNTED |  | YES | Bogani | KBC TRANSMITTER | 0.0315 | YES | 400 |  |  |  |  | Legal
36.7659 | -1.3649 | node12 |  |  |  |  | -1 | 0 | -1 | [9 empty] | node12 | node12 | 36.7659 | -1.3649 | 300755619 |  |  | 175528 - CATHOLIC UNIVERSITY | ( CODE 2 ) - SUBSTATION |  | 100 | M.V. EARTHING INSTALLATION | L.V. EARTHING INSTALLATION |  |  | L.V. SUBSTATION LEADS FOR<= 200 KVA GMT 3(1X300)+1(1X300) |  | 29/01/2019 11:41:54 | kpl17659m | kpl17659m |  |  | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA | OUTDOOR | 1 | 1 |  |  |  |  | H POLE |  | NO |  | KAREN | 0.011 |  | 55 | 0
36.7674 | -1.3682 | node13 |  |  |  |  | -1 | 0 | -1 | [9 empty] | node13 | node13 | 36.7674 | -1.3682 | 300713564 |  | 04/05/2017 | 136305 - NORKAN S.TREATMENT P | ( CODE 2 ) - SUBSTATION |  | 200 | [6 empty] | 25/09/2018 13:32:08 |  |  |  |  | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA | OUTDOOR | 4 | 4 |  |  |  |  | H POLE |  | YES |  | HARDY | 0.7089 |  | 3093 | 0
36.7671 | -1.37 | node14 |  |  |  |  | -1 | 0 | -1 | [9 empty] | node14 | node14 | 36.7671 | -1.37 | 300749021 |  |  | 169238 - CAMBRIDGE | ( CODE 2 ) - SUBSTATION |  | 1000 | [6 empty] | 21/09/2018 15:04:53 |  |  |  |  | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA | INDOOR | 1 | 1 |  | TAPLINS |  |  | GROUND MOUNTED |  | YES | OFF MAGADI RD | CAMBRIDGE | 0.0124 |  | 600 | 0
36.7692 | -1.3759 | node15 |  |  |  |  | -1 | 0 | -1 | [9 empty] | node15 | node15 | 36.7692 | -1.3759 | 300639618 |  | 24/05/2012 | 00408 - MAGADI ROAD | ( CODE 0 ) - NON-C.W.S. |  | 200 |  |  | 0 | 18 |  | 08/05/2015 06:58:46 | 21/09/2018 16:52:29 |  |  | 1020_POT_INS | HAEXLANGATA | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA | OUTDOOR | 28 | 29 | 0 | TAPLINS | KPLC |  | H POLE | 60 | YES | PAPAI ROAD | OPPOSITE SWARA SAFARI HOTEL | 2.1551 | YES | 6958 | 3.3 | 955.3 | 6.6
36.7582 | -1.3754 | node16 |  |  |  |  | -1 | 0 | -1 | [9 empty] | node16 | node16 | 36.7582 | -1.3754 | 300702064 |  |  | 106600 - 106600 | UNKNOWN |  | 315 | [5 empty] | 14/11/2015 11:27:41 | 21/11/2018 09:29:26 |  | kpl17660 |  |  | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA |  | 9 | 11 | [6 empty] | YES | Magadi road | Sisters residence CUEA | 0.7128 | YES | 16009 | 0
36.7579 | -1.3732 | node17 |  |  |  |  | -1 | 0 | -1 | [9 empty] | node17 | node17 | 36.7579 | -1.3732 | 300002119 |  | 24/05/2012 | 13708 - ST. AQUINAS SEMINARY | UNKNOWN |  | 100 |  |  | 0 | 82 |  | 19/05/2015 04:09:29 | 02/10/2018 11:19:18 |  |  | 1020_POT_INS | HRDY EX | LANGATA 66KV / 11KV | HARDY EX LANGATA | 208001428 | LANGATA |  | 7 | 7 | 0 | FUSES | KPLC |  |  | 100 | YES | blessed bakanja road | blessed bakanja | 0.7021 | YES | 83 | 8.5 | 1219.9 | 8.5
36.7586 | -1.3789 | node18 |  |  |  |  | -1 | 0 | -1 | [9 empty] | node18 | node18 | 36.7586 | -1.3789
36.7612 | -1.3826 | node19 |  |  |  |  | -1 | 0 | -1 | [9 empty] | node19 | node19 | 36.7612 | -1.3826
36.7411 | -1.3752 | node2 |  |  |  |  | -1 | 0 | -1 | [9 empty] | node2 | node2 | 36.7411 | -1.3752
36.7463 | -1.3745 | node20 |  |  |  |  | -1 | 0 | -1 | [9 empty] | node20 | node20 | 36.7463 | -1.3745
36.7463 | -1.3808 | node21 |  |  |  |  | -1 | 0 | -1 | [9 empty] | node21 | node21 | 36.7463 | -1.3808
36.7555 | -1.357 | node22 |  |  |  |  | -1 | 0 | -1 | [9 empty] | node22 | node22 | 36.7555 | -1.357
36.7558 | -1.3631 | node23 |  |  |  |  | -1 | 0 | -1 | [9 empty] | node23 | node23 | 36.7558 | -1.3631
36.7637 | -1.3622 | node24 |  |  |  |  | -1 | 0 | -1 | [9 empty] | node24 | node24 | 36.7637 | -1.3622
36.7647 | -1.3633 | node25 |  |  |  |  | -1 | 0 | -1 | [9 empty] | node25 | node25 | 36.7647 | -1.3633
36.757 | -1.3493 | node26 |  |  |  |  | -1 | 0 | -1 | [9 empty] | node26 | node26 | 36.757 | -1.3493
36.7564 | -1.3528 | node3 |  |  |  |  | -1 | 0 | -1 | [9 empty] | node3 | node3 | 36.7564 | -1.3528
36.7589 | -1.3525 | node4 |  |  |  |  | -1 | 0 | -1 | [9 empty] | node4 | node4 | 36.7589 | -1.3525
36.7603 | -1.3524 | node5 |  |  |  |  | -1 | 0 | -1 | [9 empty] | node5 | node5 | 36.7603 | -1.3524
36.7624 | -1.3519 | node6 |  |  |  |  | -1 | 0 | -1 | [9 empty] | node6 | node6 | 36.7624 | -1.3519
36.7634 | -1.3467 | node6a |  |  |  |  | -1 | 0 | -1 | [9 empty] | node6a | node6a | 36.7634 | -1.3467
36.7618 | -1.3558 | node6b |  |  |  |  | -1 | 0 | -1 | [9 empty] | node6b | node6b | 36.7618 | -1.3558
36.7652 | -1.3466 | node7 |  |  |  |  | -1 | 0 | -1 | [9 empty] | node7 | node7 | 36.7652 | -1.3466
36.7621 | -1.3567 | node8 |  |  |  |  | -1 | 0 | -1 | [9 empty] | node8 | node8 | 36.7621 | -1.3567
36.7624 | -1.3589 | node9 |  |  |  |  | -1 | 0 | -1 | [9 empty] | node9 | node9 | 36.7624 | -1.3589
36.7568 | -1.3469 | 136305 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Langa'Ta | 136305 | NORKAN S.TREATMENT PLANT | 36.7568 | -1.3469
36.7618 | -1.3559 | 12105 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Hardy | 12105 | PARK PLACE HOTEL | 36.7618 | -1.3559
36.7472 | -1.381 | 3907 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Hardy | 3907 | PARK VIEW EST._LANGATA | 36.7472 | -1.381
36.7466 | -1.3745 | 446 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Hardy | 446 | PARK VIEW_LANGATA | 36.7466 | -1.3745
36.7638 | -1.3621 | 32287 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Mugumoini | Bomas | 32287 | SAIFEE PARK_MAGADI RD_0 | 36.7638 | -1.3621
36.7618 | -1.3618 | 455 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Hardy | 455 | SAIFEE PARK_MAGADI RD_I | 36.7618 | -1.3618
36.7411 | -1.3742 | 33950 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Hardy | 33950 | SIMBA HILL ROAD_0 | 36.7411 | -1.3742
36.7412 | -1.3773 | 447 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Hardy | 447 | SIMBA HILL ROAD_I | 36.7412 | -1.3773
36.754 | -1.3472 | 13708 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Langa'Ta | 13708 | ST. AQUINAS SEMINARY | 36.754 | -1.3472
36.7586 | -1.3487 | 404 |  |  |  |  | -1 | 0 | -1 |  |  | Nairobi |  |  |  | Langata | Langa'Ta | Langa'Ta | 404 | ST.THOMAS SEMINARY | 36.7586 | -1.3487

## snapped_lines
WKT | Name | timestamp | begin | end | altitudeMo | tessellate | extrude | visibility | drawOrder | icon | snippet | layer | path | LINE_NO | Location | Sub Locati | Fuse Code | Internal C | length_km | MV line se | geos | Internal_1 | Switch Num | Secondary | Taplin Cod
LINESTRING Z (36.7582431679171 -1.37584084408693 0,36.7582431679171 -1.37584084408693 0) | [5 empty] | -1 | 0 | -1 |  |  | 998808788 | hardy HT FUSE | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=HT FUSE | 1 | Langa'Ta | Hardy | F007 | 998808788 | 0 |  | LINESTRING Z (36.7582431679171 -1.37584084408693 0,36.7582431679171 -1.37584084408693 0)
LINESTRING Z (36.7465582726068 -1.37450408676786 0,36.7465582726068 -1.37450408676786 0) | [5 empty] | -1 | 0 | -1 |  |  | 311000954 | hardy HT FUSE | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=HT FUSE | 2 | Langa'Ta | Hardy | F030 | 311000954 | 0 |  | LINESTRING Z (36.7465582726068 -1.37450408676786 0,36.7465582726068 -1.37450408676786 0)
LINESTRING Z (36.7554608025107 -1.35688558713458 0,36.7554608025107 -1.35688558713458 0) | [5 empty] | -1 | 0 | -1 |  |  | 998858798 | hardy HT FUSE | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=HT FUSE | 3 | Langa'Ta | Hardy |  | 998858798 | 0 |  | LINESTRING Z (36.7554608025107 -1.35688558713458 0,36.7554608025107 -1.35688558713458 0)
LINESTRING Z (36.7605795763563 -1.35286426923963 0,36.7605795763563 -1.35286426923963 0) | [5 empty] | -1 | 0 | -1 |  |  | 998858818 | hardy HT FUSE | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=HT FUSE | 4 | Langa'Ta | Langa'Ta |  | 998858818 | 0 |  | LINESTRING Z (36.7605795763563 -1.35286426923963 0,36.7605795763563 -1.35286426923963 0)
LINESTRING Z (36.76591701561 -1.36494782278443 0,36.76591701561 -1.36494782278443 0) | [5 empty] | -1 | 0 | -1 |  |  | 998864670 | hardy HT FUSE | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=HT FUSE | 5 | Mugumoini | Bomas |  | 998864670 | 0 |  | LINESTRING Z (36.76591701561 -1.36494782278443 0,36.76591701561 -1.36494782278443 0)
LINESTRING Z (36.7589102901439 -1.35254987804557 0,36.7589102901439 -1.35254987804557 0) | [5 empty] | -1 | 0 | -1 |  |  | 998864555 | hardy HT FUSE | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=HT FUSE | 6 | Langa'Ta | Langa'Ta |  | 998864555 | 0 |  | LINESTRING Z (36.7589102901439 -1.35254987804557 0,36.7589102901439 -1.35254987804557 0)
LINESTRING Z (36.7673984075653 -1.36823663832402 0,36.7673984075653 -1.36823663832402 0) | [5 empty] | -1 | 0 | -1 |  |  | 998864671 | hardy HT FUSE | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=HT FUSE | 7 | Langa'Ta | Hardy |  | 998864671 | 0 |  | LINESTRING Z (36.7673984075653 -1.36823663832402 0,36.7673984075653 -1.36823663832402 0)
LINESTRING Z (36.7545773444594 -1.36095430482037 0,36.7545773444594 -1.36095430482037 0) | [5 empty] | -1 | 0 | -1 |  |  | 998864668 | hardy HT FUSE | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=HT FUSE | 8 | Langa'Ta | Hardy |  | 998864668 | 0 |  | LINESTRING Z (36.7545773444594 -1.36095430482037 0,36.7545773444594 -1.36095430482037 0)
LINESTRING Z (36.7654302091879 -1.34598825744552 0,36.7654302091879 -1.34598825744552 0) | [5 empty] | -1 | 0 | -1 |  |  | 998818308 | hardy HT FUSE | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=HT FUSE | 9 | Langa'Ta | Langa'Ta | F010 | 998818308 | 0 |  | LINESTRING Z (36.7654302091879 -1.34598825744552 0,36.7654302091879 -1.34598825744552 0)
LINESTRING Z (36.7586495558373 -1.34867344535816 0,36.7586495558373 -1.34867344535816 0) | [5 empty] | -1 | 0 | -1 |  |  | 998817705 | hardy HT FUSE | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=HT FUSE | 10 | Langa'Ta | Langa'Ta | F004 | 998817705 | 0 |  | LINESTRING Z (36.7586495558373 -1.34867344535816 0,36.7586495558373 -1.34867344535816 0)
LINESTRING Z (36.7612068626399 -1.37964570579744 0,36.7612068626399 -1.37964570579744 0) | [5 empty] | -1 | 0 | -1 |  |  | 998808785 | hardy HT FUSE | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=HT FUSE | 11 | Langa'Ta | Hardy | F009 | 998808785 | 0 |  | LINESTRING Z (36.7612068626399 -1.37964570579744 0,36.7612068626399 -1.37964570579744 0)
LINESTRING Z (36.7616185428589 -1.35672560455267 0,36.7616185428589 -1.35672560455267 0) | [5 empty] | -1 | 0 | -1 |  |  | 998857255 | hardy HT FUSE | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=HT FUSE | 12 | Langa'Ta | Hardy |  | 998857255 | 0 |  | LINESTRING Z (36.7616185428589 -1.35672560455267 0,36.7616185428589 -1.35672560455267 0)
LINESTRING Z (36.7649949841971 -1.36363436841892 0,36.7649949841971 -1.36363436841892 0) | [5 empty] | -1 | 0 | -1 |  |  | 311600282 | hardy HT FUSE | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=HT FUSE | 13 | Mugumoini | Bomas | F007 | 311600282 | 0 |  | LINESTRING Z (36.7649949841971 -1.36363436841892 0,36.7649949841971 -1.36363436841892 0)
LINESTRING Z (36.7567183085312 -1.38099466561844 0,36.7567183085312 -1.38099466561844 0) | [5 empty] | -1 | 0 | -1 |  |  | 998819192 | hardy HT FUSE | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=HT FUSE | 14 | Langa'Ta | Hardy | F009 | 998819192 | 0 |  | LINESTRING Z (36.7567183085312 -1.38099466561844 0,36.7567183085312 -1.38099466561844 0)
LINESTRING Z (36.7651574651075 -1.34656776213099 0,36.7651574651075 -1.34656776213099 0) | [5 empty] | -1 | 0 | -1 |  |  | 998864667 | hardy HT FUSE | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=HT FUSE | 15 | Langa'Ta | Langa'Ta |  | 998864667 | 0 |  | LINESTRING Z (36.7651574651075 -1.34656776213099 0,36.7651574651075 -1.34656776213099 0)
LINESTRING Z (36.7624931584252 -1.3609281124923 0,36.7624931584252 -1.3609281124923 0) | [5 empty] | -1 | 0 | -1 |  |  | 998864669 | hardy HT FUSE | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=HT FUSE | 16 | Langa'Ta | Hardy |  | 998864669 | 0 |  | LINESTRING Z (36.7624931584252 -1.3609281124923 0,36.7624931584252 -1.3609281124923 0)
LINESTRING Z (36.7577418860007 -1.34328854424595 0,36.7577418860007 -1.34328854424595 0) | [5 empty] | -1 | 0 | -1 |  |  | 998851024 | hardy HT FUSE | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=HT FUSE | 17 | Langa'Ta | Langa'Ta |  | 998851024 | 0 |  | LINESTRING Z (36.7577418860007 -1.34328854424595 0,36.7577418860007 -1.34328854424595 0)
LINESTRING Z (36.7698813824731 -1.38001194403103 0,36.7698813824731 -1.38001194403103 0) | [5 empty] | -1 | 0 | -1 |  |  | 998851027 | hardy HT FUSE | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=HT FUSE | 18 | Langa'Ta | Hardy |  | 998851027 | 0 |  | LINESTRING Z (36.7698813824731 -1.38001194403103 0,36.7698813824731 -1.38001194403103 0)
LINESTRING Z (36.7554793265145 -1.3571046954011 0,36.7555190442461 -1.35702584112019 0) | [5 empty] | -1 | 0 | -1 |  |  | 998854393 | hardy HT FUSE | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=HT FUSE | 19 | Langa'Ta | Hardy |  | 998854393 | 0.01 |  | LINESTRING Z (36.7554793265145 -1.3571046954011 0,36.7555190442461 -1.35702584112019 0)
LINESTRING Z (36.756256521237 -1.35172476577396 0,36.756256521237 -1.35172476577396 0) | F062 |  |  |  |  | -1 | 0 | -1 |  |  | 311000975 | hardy HT FUSE | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=HT FUSE | 20 | Langa'Ta | Langa'Ta | F002 | 311000975 | 0 |  | LINESTRING Z (36.756256521237 -1.35172476577396 0,36.756256521237 -1.35172476577396 0)
LINESTRING Z (36.7567865754473 -1.37905058253932 0,36.7567865754473 -1.37905058253932 0) | [5 empty] | -1 | 0 | -1 |  |  | 998808787 | hardy HT FUSE | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=HT FUSE | 21 | Langa'Ta | Hardy | F008 | 998808787 | 0 |  | LINESTRING Z (36.7567865754473 -1.37905058253932 0,36.7567865754473 -1.37905058253932 0)
LINESTRING Z (36.7531188035318 -1.35326474608744 0,36.7531188035318 -1.35326474608744 0) | F064 |  |  |  |  | -1 | 0 | -1 |  |  | 311000777 | hardy HT FUSE | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=HT FUSE | 22 | Langa'Ta | Langa'Ta | F003 | 311000777 | 0 |  | LINESTRING Z (36.7531188035318 -1.35326474608744 0,36.7531188035318 -1.35326474608744 0)
LINESTRING Z (36.7748666444081 -1.37859409878224 0,36.7748666444081 -1.37859409878224 0) | [5 empty] | -1 | 0 | -1 |  |  | 311000807 | hardy HT FUSE | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=HT FUSE | 23 | Mugumoini | Bomas | F008 | 311000807 | 0 |  | LINESTRING Z (36.7748666444081 -1.37859409878224 0,36.7748666444081 -1.37859409878224 0)
LINESTRING Z (36.7565940277503 -1.36136318895282 0,36.7565940277503 -1.36136318895282 0) | [5 empty] | -1 | 0 | -1 |  |  | 998815747 | hardy HT FUSE | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=HT FUSE | 24 | Langa'Ta | Hardy | F006 | 998815747 | 0 |  | LINESTRING Z (36.7565940277503 -1.36136318895282 0,36.7565940277503 -1.36136318895282 0)
LINESTRING Z (36.7612165638942 -1.38254550565052 0,36.7612165638942 -1.38254550565052 0) | [5 empty] | -1 | 0 | -1 |  |  | 998808784 | hardy HT FUSE | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=HT FUSE | 25 | Langa'Ta | Hardy | F068 | 998808784 | 0 |  | LINESTRING Z (36.7612165638942 -1.38254550565052 0,36.7612165638942 -1.38254550565052 0)
LINESTRING Z (36.7539687234416 -1.34724283485521 0,36.7539687234416 -1.34724283485521 0) | [5 empty] | -1 | 0 | -1 |  |  | 311000966 | hardy HT FUSE | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=HT FUSE | 26 | Langa'Ta | Langa'Ta | F001 | 311000966 | 0 |  | LINESTRING Z (36.7539687234416 -1.34724283485521 0,36.7539687234416 -1.34724283485521 0)
LINESTRING Z (36.763036432869 -1.35049720568309 0,36.763036432869 -1.35049720568309 0) | F058 |  |  |  |  | -1 | 0 | -1 |  |  | 311000772 | hardy HT FUSE | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=HT FUSE | 27 | Langa'Ta | Langa'Ta | F005 | 311000772 | 0 |  | LINESTRING Z (36.763036432869 -1.35049720568309 0,36.763036432869 -1.35049720568309 0)
LINESTRING Z (36.7602629004934 -1.37549780111096 0,36.7602629004934 -1.37549780111096 0) | [5 empty] | -1 | 0 | -1 |  |  | 998813859 | hardy HT FUSE | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=HT FUSE | 28 | Langa'Ta | Hardy | F006 | 998813859 | 0 |  | LINESTRING Z (36.7602629004934 -1.37549780111096 0,36.7602629004934 -1.37549780111096 0)
LINESTRING Z (36.7732945605242 -1.37963397207946 0,36.7732945605242 -1.37963397207946 0) | [5 empty] | -1 | 0 | -1 |  |  | 311600118 | hardy HT FUSE | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=HT FUSE | 29 | Mugumoini | Bomas | TP018 | 311600118 | 0 |  | LINESTRING Z (36.7732945605242 -1.37963397207946 0,36.7732945605242 -1.37963397207946 0)
LINESTRING Z (36.7603337106913 -1.35236395032121 0,36.7603337106913 -1.35236395032121 0) | [5 empty] | -1 | 0 | -1 |  |  | 998864557 | hardy HT FUSE | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=HT FUSE | 30 | Langa'Ta | Langa'Ta |  | 998864557 | 0 |  | LINESTRING Z (36.7603337106913 -1.35236395032121 0,36.7603337106913 -1.35236395032121 0)
LINESTRING Z (36.7412361387439 -1.37728738234144 0,36.7412361387439 -1.37728738234144 0) | [5 empty] | -1 | 0 | -1 |  |  | 998829676 | hardy HT FUSE | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=HT FUSE | 31 | Langa'Ta | Hardy |  | 998829676 | 0 |  | LINESTRING Z (36.7412361387439 -1.37728738234144 0,36.7412361387439 -1.37728738234144 0)
LINESTRING Z (36.7612068626399 -1.37964570579744 0,36.7644866512733 -1.37824857283834 0) | KLGLS084 |  |  |  |  | -1 | 0 | -1 |  |  | 301004291 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 32 | 10602010602 | 1060201060201 |  |  | 0.397 | 10024:1 | LINESTRING Z (36.7612068626399 -1.37964570579744 0,36.7644866512733 -1.37824857283834 0)
LINESTRING Z (36.763526981731 -1.36789570407714 0,36.7608369568325 -1.36805173513509 0) | [5 empty] | -1 | 0 | -1 |  |  | 301661322 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 33 | 10602010602 | 1060201060201 |  |  | 0.3 | UNKNOWN | LINESTRING Z (36.763526981731 -1.36789570407714 0,36.7608369568325 -1.36805173513509 0)
LINESTRING Z (36.7667231620065 -1.38047793835761 0,36.7667231620065 -1.38047793835761 0) | [5 empty] | -1 | 0 | -1 |  |  | 301003587 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 34 | 10602010602 | 1060201060201 |  |  | 0 | 10024:10 | LINESTRING Z (36.7667231620065 -1.38047793835761 0,36.7667231620065 -1.38047793835761 0)
LINESTRING Z (36.7692169954759 -1.37588183070028 0,36.7681820421319 -1.37197221229169 0) | [5 empty] | -1 | 0 | -1 |  |  | 301003581 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 35 | 10602010603 | 1060201060301 |  |  | 0.45 | UNKNOWN | LINESTRING Z (36.7692169954759 -1.37588183070028 0,36.7681820421319 -1.37197221229169 0)
LINESTRING Z (36.7462733180924 -1.37453872997444 0,36.7465582726068 -1.37450408676786 0) | KLGLS072 |  |  |  |  | -1 | 0 | -1 |  |  | 301004262 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 36 | 10602010602 | 1060201060201 |  |  | 0.032 | UNKNOWN | LINESTRING Z (36.7462733180924 -1.37453872997444 0,36.7465582726068 -1.37450408676786 0)
LINESTRING Z (36.7545773444594 -1.36095430482037 0) | [5 empty] | -1 | 0 | -1 |  |  | 301730772 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 37 | 10602010602 | 1060201060201 |  |  | 0 |  | LINESTRING Z (36.7545773444594 -1.36095430482037 0)
LINESTRING Z (36.7462733180924 -1.37453872997444 0,36.7462733180924 -1.37453872997444 0) | KLGLS069 |  |  |  |  | -1 | 0 | -1 |  |  | 301004257 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 38 | 10602010602 | 1060201060201 |  |  | 0 | UNKNOWN | LINESTRING Z (36.7462733180924 -1.37453872997444 0,36.7462733180924 -1.37453872997444 0)
LINESTRING Z (36.7565940277503 -1.36136318895282 0,36.7565940277503 -1.36136318895282 0) | [5 empty] | -1 | 0 | -1 |  |  | 301913126 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 39 | 10602010602 | 1060201060201 |  |  | 0 | UNKNOWN | LINESTRING Z (36.7565940277503 -1.36136318895282 0,36.7565940277503 -1.36136318895282 0)
LINESTRING Z (36.7503475000925 -1.35358701297463 0,36.7471094242747 -1.35713395967179 0) | NLGLS139 |  |  |  |  | -1 | 0 | -1 |  |  | 301003523 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 40 | Langa'Ta | Langa'Ta |  |  | 0.535 | UNKNOWN | LINESTRING Z (36.7503475000925 -1.35358701297463 0,36.7471094242747 -1.35713395967179 0)
LINESTRING Z (36.7698813824731 -1.38001194403103 0) | [5 empty] | -1 | 0 | -1 |  |  | 301913131 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 41 | 10602010602 | 1060201060201 |  |  | 0 | UNKNOWN | LINESTRING Z (36.7698813824731 -1.38001194403103 0)
LINESTRING Z (36.7698813824731 -1.38001194403103 0,36.7732945605242 -1.37963397207946 0) | [5 empty] | -1 | 0 | -1 |  |  | 301003582 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 42 | 10602010603 | 1060201060301 |  |  | 0.382 | UNKNOWN | LINESTRING Z (36.7698813824731 -1.38001194403103 0,36.7732945605242 -1.37963397207946 0)
LINESTRING Z (36.7586892630442 -1.38004691996939 0,36.7612068626399 -1.37964570579744 0) | KLGLS082 |  |  |  |  | -1 | 0 | -1 |  |  | 301913135 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 43 | 10602010602 | 1060201060201 |  |  | 0.284 | UNKNOWN | LINESTRING Z (36.7586892630442 -1.38004691996939 0,36.7612068626399 -1.37964570579744 0)
LINESTRING Z (36.76591701561 -1.36494782278443 0,36.7673305364644 -1.36377539781515 0) | [5 empty] | -1 | 0 | -1 |  |  | 301003545 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 44 | 10602010603 | 1060201060301 |  |  | 0.204 | UNKNOWN | LINESTRING Z (36.76591701561 -1.36494782278443 0,36.7673305364644 -1.36377539781515 0)
LINESTRING Z (36.7582431679171 -1.37584084408693 0,36.7585500007543 -1.3788663993872 0) | KLGLS080 |  |  |  |  | -1 | 0 | -1 |  |  | 301659723 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 45 | Langa'Ta | Hardy |  |  | 0.339 | UNKNOWN | LINESTRING Z (36.7582431679171 -1.37584084408693 0,36.7585500007543 -1.3788663993872 0)
LINESTRING Z (36.7579264893446 -1.37349144029173 0,36.7581961720968 -1.37541704664815 0) | KLGLS077 |  |  |  |  | -1 | 0 | -1 |  |  | 301004274 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 46 | Langa'Ta | Hardy |  |  | 0.216 | UNKNOWN | LINESTRING Z (36.7579264893446 -1.37349144029173 0,36.7581961720968 -1.37541704664815 0)
LINESTRING Z (36.762076283107 -1.34714933688208 0,36.7633764169857 -1.34667459800873 0) | [5 empty] | -1 | 0 | -1 |  |  | 30746 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 47 | 10602010602 | 1060201060202 |  |  | 0.154 | UNKNOWN | LINESTRING Z (36.762076283107 -1.34714933688208 0,36.7633764169857 -1.34667459800873 0)
LINESTRING Z (36.7465582726068 -1.37450408676786 0,36.7505226572627 -1.37408454262385 0) | KLGLS072 |  |  |  |  | -1 | 0 | -1 |  |  | 301685155 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 48 | 10602010602 | 1060201060201 |  |  | 0.444 | UNKNOWN | LINESTRING Z (36.7465582726068 -1.37450408676786 0,36.7505226572627 -1.37408454262385 0)
LINESTRING Z (36.7654302091879 -1.34598825744552 0) | NLGLS125 |  |  |  |  | -1 | 0 | -1 |  |  | 301686311 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 49 | 10602010602 | 1060201060202 |  |  | 0 | UNKNOWN | LINESTRING Z (36.7654302091879 -1.34598825744552 0)
LINESTRING Z (36.7568232402855 -1.34692593186729 0,36.7577418860007 -1.34328854424595 0) | KLGLS102 |  |  |  |  | -1 | 0 | -1 |  |  | 301004314 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 50 | 10602010602 | 1060201060202 |  |  | 0.418 | UNKNOWN | LINESTRING Z (36.7568232402855 -1.34692593186729 0,36.7577418860007 -1.34328854424595 0)
LINESTRING Z (36.7673984075653 -1.36823663832402 0) | [5 empty] | -1 | 0 | -1 |  |  | 301003557 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 51 | Langa'Ta | Hardy |  |  | 0 | UNKNOWN | LINESTRING Z (36.7673984075653 -1.36823663832402 0)
LINESTRING Z (36.7568232402855 -1.34692593186729 0,36.7570291160282 -1.34932128908751 0) | [5 empty] | -1 | 0 | -1 |  |  | 301685113 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 52 | 10602010602 | 1060201060202 |  |  | 0.268 | UNKNOWN | LINESTRING Z (36.7568232402855 -1.34692593186729 0,36.7570291160282 -1.34932128908751 0)
LINESTRING Z (36.7570291160282 -1.34932128908751 0,36.757891416378 -1.3499707011205 0) | [5 empty] | -1 | 0 | -1 |  |  | 301685114 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 53 | 10602010602 | 1060201060202 |  |  | 0.12 | UNKNOWN | LINESTRING Z (36.7570291160282 -1.34932128908751 0,36.757891416378 -1.3499707011205 0)
LINESTRING Z (36.757891416378 -1.3499707011205 0,36.757891416378 -1.3499707011205 0) | [5 empty] | -1 | 0 | -1 |  |  | 301685115 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 54 | 10602010602 | 1060201060202 |  |  | 0 | UNKNOWN | LINESTRING Z (36.757891416378 -1.3499707011205 0,36.757891416378 -1.3499707011205 0)
LINESTRING Z (36.7570291160282 -1.34932128908751 0,36.7563236410844 -1.35075336316955 0) | [5 empty] | -1 | 0 | -1 |  |  | 301685117 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 55 | 10602010602 | 1060201060202 |  |  | 0.178 | UNKNOWN | LINESTRING Z (36.7570291160282 -1.34932128908751 0,36.7563236410844 -1.35075336316955 0)
LINESTRING Z (36.7589102901439 -1.35254987804557 0,36.7569132002294 -1.35272869876763 0) | NLGLS131 |  |  |  |  | -1 | 0 | -1 |  |  | 301003508 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 56 | 10602010602 | 1060201060202 |  |  | 0.223 | UNKNOWN | LINESTRING Z (36.7589102901439 -1.35254987804557 0,36.7569132002294 -1.35272869876763 0)
LINESTRING Z (36.756256521237 -1.35172476577396 0) | [5 empty] | -1 | 0 | -1 |  |  | 301685121 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 57 | 10602010602 | 1060201060202 |  |  | 0 | UNKNOWN | LINESTRING Z (36.756256521237 -1.35172476577396 0)
LINESTRING Z (36.7569132002294 -1.35272869876763 0) | [5 empty] | -1 | 0 | -1 |  |  | 301685122 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 58 | 10602010602 | 1060201060202 |  |  | 0 | UNKNOWN | LINESTRING Z (36.7569132002294 -1.35272869876763 0)
LINESTRING Z (36.7624931584252 -1.3609281124923 0,36.7622855261742 -1.36069603276204 0) | [5 empty] | -1 | 0 | -1 |  |  | 301687265 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 59 | 10602010602 | 1060201060201 |  |  | 0.035 | UNKNOWN | LINESTRING Z (36.7624931584252 -1.3609281124923 0,36.7622855261742 -1.36069603276204 0)
LINESTRING Z (36.7622855261742 -1.36069603276204 0,36.7624322359531 -1.35891324510337 0) | [5 empty] | -1 | 0 | -1 |  |  | 301003533 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 60 | 10602010602 | 1060201060201 |  |  | 0.199 | UNKNOWN | LINESTRING Z (36.7622855261742 -1.36069603276204 0,36.7624322359531 -1.35891324510337 0)
LINESTRING Z (36.7563236410844 -1.35075336316955 0,36.7563236410844 -1.35075336316955 0) | [5 empty] | -1 | 0 | -1 |  |  | 301685118 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 61 | 10602010602 | 1060201060202 |  |  | 0 | UNKNOWN | LINESTRING Z (36.7563236410844 -1.35075336316955 0,36.7563236410844 -1.35075336316955 0)
LINESTRING Z (36.7563236410844 -1.35075336316955 0,36.756256521237 -1.35172476577396 0) | [5 empty] | -1 | 0 | -1 |  |  | 301685120 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 62 | 10602010602 | 1060201060202 |  |  | 0.108 | UNKNOWN | LINESTRING Z (36.7563236410844 -1.35075336316955 0,36.756256521237 -1.35172476577396 0)
LINESTRING Z (36.7681820421319 -1.37197221229169 0,36.7681820421319 -1.37197221229169 0) | [5 empty] | -1 | 0 | -1 |  |  | 301003577 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 63 | Langa'Ta | Hardy |  |  | 0 | UNKNOWN | LINESTRING Z (36.7681820421319 -1.37197221229169 0,36.7681820421319 -1.37197221229169 0)
LINESTRING Z (36.7505226572627 -1.37408454262385 0,36.757888759798 -1.37319733022595 0) | KLGLS073 |  |  |  |  | -1 | 0 | -1 |  |  | 301004265 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 64 | 10602010602 | 1060201060201 |  |  | 0.826 | UNKNOWN | LINESTRING Z (36.7505226572627 -1.37408454262385 0,36.757888759798 -1.37319733022595 0)
LINESTRING Z (36.7698813824731 -1.38001194403103 0) | [5 empty] | -1 | 0 | -1 |  |  | 301684651 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 65 | 10602010602 | 1060201060201 |  |  | 0 | UNKNOWN | LINESTRING Z (36.7698813824731 -1.38001194403103 0)
LINESTRING Z (36.7651574651075 -1.34656776213099 0,36.7654302091879 -1.34598825744552 0) | NLGLS125 |  |  |  |  | -1 | 0 | -1 |  |  | 301003490 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 66 | 10602010602 | 1060201060202 |  |  | 0.071 | UNKNOWN | LINESTRING Z (36.7651574651075 -1.34656776213099 0,36.7654302091879 -1.34598825744552 0)
LINESTRING Z (36.7681820421319 -1.37197221229169 0,36.7681820421319 -1.37197221229169 0) | [5 empty] | -1 | 0 | -1 |  |  | 301003579 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 67 | Langa'Ta | Hardy |  |  | 0 | UNKNOWN | LINESTRING Z (36.7681820421319 -1.37197221229169 0,36.7681820421319 -1.37197221229169 0)
LINESTRING Z (36.7673984075653 -1.36823663832402 0,36.7666444907395 -1.36618876197399 0) | [5 empty] | -1 | 0 | -1 |  |  | 301003551 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 68 | 10602010603 | 1060201060301 |  |  | 0.243 | UNKNOWN | LINESTRING Z (36.7673984075653 -1.36823663832402 0,36.7666444907395 -1.36618876197399 0)
LINESTRING Z (36.7666444907395 -1.36618876197399 0,36.76591701561 -1.36494782278443 0) | [5 empty] | -1 | 0 | -1 |  |  | 301003548 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 69 | 10602010603 | 1060201060301 |  |  | 0.16 | UNKNOWN | LINESTRING Z (36.7666444907395 -1.36618876197399 0,36.76591701561 -1.36494782278443 0)
LINESTRING Z (36.7673984075653 -1.36823663832402 0,36.763526981731 -1.36789570407714 0) | [5 empty] | -1 | 0 | -1 |  |  | 301003565 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 70 | 10602010602 | 1060201060201 |  |  | 0.433 | UNKNOWN | LINESTRING Z (36.7673984075653 -1.36823663832402 0,36.763526981731 -1.36789570407714 0)
LINESTRING Z (36.7575736263158 -1.36825584429273 0,36.7565958938682 -1.36954724767579 0) | [5 empty] | -1 | 0 | -1 |  |  | 301661324 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 71 | 10602010602 | 1060201060201 |  |  | 0.18 | UNKNOWN | LINESTRING Z (36.7575736263158 -1.36825584429273 0,36.7565958938682 -1.36954724767579 0)
LINESTRING Z (36.7732945605242 -1.37963397207946 0,36.7748666444081 -1.37859409878224 0) | [5 empty] | -1 | 0 | -1 |  |  | 301685150 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 72 | 10602010603 | 1060201060301 |  |  | 0.21 | UNKNOWN | LINESTRING Z (36.7732945605242 -1.37963397207946 0,36.7748666444081 -1.37859409878224 0)
LINESTRING Z (36.7594311309821 -1.36389019607431 0,36.7594311309821 -1.36389019607431 0) | [5 empty] | -1 | 0 | -1 |  |  | 301678569 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 73 | Langa'Ta | Hardy |  |  | 0 | UNKNOWN | LINESTRING Z (36.7594311309821 -1.36389019607431 0,36.7594311309821 -1.36389019607431 0)
LINESTRING Z (36.7579665525604 -1.34209999724138 0,36.7577418860007 -1.34328854424595 0) | [5 empty] | -1 | 0 | -1 |  |  | 301685106 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 74 | 10602010602 | 1060201060202 |  |  | 0.135 | UNKNOWN | LINESTRING Z (36.7579665525604 -1.34209999724138 0,36.7577418860007 -1.34328854424595 0)
LINESTRING Z (36.7558333036587 -1.36313160563965 0,36.7565940277503 -1.36136318895282 0) | [5 empty] | -1 | 0 | -1 |  |  | 301913125 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 75 | 10602010602 | 1060201060201 |  |  | 0.214 | UNKNOWN | LINESTRING Z (36.7558333036587 -1.36313160563965 0,36.7565940277503 -1.36136318895282 0)
LINESTRING Z (36.7579665525604 -1.34209999724138 0) | [5 empty] | -1 | 0 | -1 |  |  | 301678127 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 76 | Langa'Ta | Langa'Ta |  |  | 0 | UNKNOWN | LINESTRING Z (36.7579665525604 -1.34209999724138 0)
LINESTRING Z (36.7565940277503 -1.36136318895282 0,36.7565940277503 -1.36136318895282 0) | [5 empty] | -1 | 0 | -1 |  |  | 301680867 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 77 | 10602010602 | 1060201060201 |  |  | 0 |  | LINESTRING Z (36.7565940277503 -1.36136318895282 0,36.7565940277503 -1.36136318895282 0)
LINESTRING Z (36.7545773444594 -1.36095430482037 0,36.7565940277503 -1.36136318895282 0) | [5 empty] | -1 | 0 | -1 |  |  | 301730776 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 78 | 10602010602 | 1060201060201 |  |  | 0.229 |  | LINESTRING Z (36.7545773444594 -1.36095430482037 0,36.7565940277503 -1.36136318895282 0)
LINESTRING Z (36.7624322359531 -1.35891324510337 0,36.7620971077276 -1.35668690737419 0) | [5 empty] | -1 | 0 | -1 |  |  | 301686583 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 79 | Langa'Ta | Hardy |  |  | 0.251 | UNKNOWN | LINESTRING Z (36.7624322359531 -1.35891324510337 0,36.7620971077276 -1.35668690737419 0)
LINESTRING Z (36.7581961720968 -1.37541704664815 0,36.7582431679171 -1.37584084408693 0) | KLGLS079 |  |  |  |  | -1 | 0 | -1 |  |  | 301004279 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 80 | 10602010602 | 1060201060201 |  |  | 0.047 | UNKNOWN | LINESTRING Z (36.7581961720968 -1.37541704664815 0,36.7582431679171 -1.37584084408693 0)
LINESTRING Z (36.7692169954759 -1.37588183070028 0,36.7698813824731 -1.38001194403103 0) | [5 empty] | -1 | 0 | -1 |  |  | 301913133 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 81 | 10602010602 | 1060201060201 |  |  | 0.466 | UNKNOWN | LINESTRING Z (36.7692169954759 -1.37588183070028 0,36.7698813824731 -1.38001194403103 0)
LINESTRING Z (36.768206929511 -1.37629011528426 0,36.7692169954759 -1.37588183070028 0) | [5 empty] | -1 | 0 | -1 |  |  | 301913134 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 82 | 10602010602 | 1060201060201 |  |  | 0.121 | UNKNOWN | LINESTRING Z (36.768206929511 -1.37629011528426 0,36.7692169954759 -1.37588183070028 0)
LINESTRING Z (36.7577418860007 -1.34328854424595 0,36.7577418860007 -1.34328854424595 0) | KLGLS101 |  |  |  |  | -1 | 0 | -1 |  |  | 301913107 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 83 | 10602010602 | 1060201060202 |  |  | 0 |  | LINESTRING Z (36.7577418860007 -1.34328854424595 0,36.7577418860007 -1.34328854424595 0)
LINESTRING Z (36.7585500007543 -1.3788663993872 0,36.7586892630442 -1.38004691996939 0) | KLGLS081 |  |  |  |  | -1 | 0 | -1 |  |  | 301004284 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 84 | 10602010602 | 1060201060201 |  |  | 0.132 | UNKNOWN | LINESTRING Z (36.7585500007543 -1.3788663993872 0,36.7586892630442 -1.38004691996939 0)
LINESTRING Z (36.7618156185011 -1.35592046277368 0,36.7617961576617 -1.35583823096373 0) | NLGLS140 |  |  |  |  | -1 | 0 | -1 |  |  | 301003526 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 85 | 10602010602 | 1060201060201 |  |  | 0.009 | UNKNOWN | LINESTRING Z (36.7618156185011 -1.35592046277368 0,36.7617961576617 -1.35583823096373 0)
LINESTRING Z (36.7581961720968 -1.37541704664815 0,36.7602629004934 -1.37549780111096 0) | KLGLS078 |  |  |  |  | -1 | 0 | -1 |  |  | 301004276 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 86 | 10602010602 | 1060201060201 |  |  | 0.23 | UNKNOWN | LINESTRING Z (36.7581961720968 -1.37541704664815 0,36.7602629004934 -1.37549780111096 0)
LINESTRING Z (36.7624223632652 -1.37265521504387 0,36.757888759798 -1.37319733022595 0) | KLGLS074 |  |  |  |  | -1 | 0 | -1 |  |  | 301004267 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 87 | 10602010602 | 1060201060201 |  |  | 0.508 | UNKNOWN | LINESTRING Z (36.7624223632652 -1.37265521504387 0,36.757888759798 -1.37319733022595 0)
LINESTRING Z (36.7654302091879 -1.34598825744552 0,36.7654302091879 -1.34598825744552 0) | NLGLS124 |  |  |  |  | -1 | 0 | -1 |  |  | 301003489 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 88 | 10602010602 | 1060201060202 |  |  | 0 | 10024:1 | LINESTRING Z (36.7654302091879 -1.34598825744552 0,36.7654302091879 -1.34598825744552 0)
LINESTRING Z (36.7471553579504 -1.38099637926356 0,36.749047924785 -1.38149034139184 0) | [5 empty] | -1 | 0 | -1 |  |  | 301676753 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 89 | 10602010602 | 1060201060201 |  |  | 0.218 | UNKNOWN | LINESTRING Z (36.7471553579504 -1.38099637926356 0,36.749047924785 -1.38149034139184 0)
LINESTRING Z (36.7603337106913 -1.35236395032121 0,36.7603337106913 -1.35236395032121 0) | [5 empty] | -1 | 0 | -1 |  |  | 30757 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 90 | Langa'Ta | Langa'Ta |  |  | 0 | UNKNOWN | LINESTRING Z (36.7603337106913 -1.35236395032121 0,36.7603337106913 -1.35236395032121 0)
LINESTRING Z (36.7651574651075 -1.34656776213099 0,36.7633764169857 -1.34667459800873 0,36.7633226633752 -1.34656625225938 0) | [5 empty] | -1 | 0 | -1 |  |  | 301686312 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 91 | Langa'Ta | Langa'Ta |  |  | 0.212 | UNKNOWN | LINESTRING Z (36.7651574651075 -1.34656776213099 0,36.7633764169857 -1.34667459800873 0,36.7633226633752 -1.34656625225938 0)
LINESTRING Z (36.7623921963995 -1.35194549133002 0,36.7603337106913 -1.35236395032121 0) | NLGLS128 |  |  |  |  | -1 | 0 | -1 |  |  | 301003498 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 92 | 10602010602 | 1060201060202 |  |  | 0.234 | UNKNOWN | LINESTRING Z (36.7623921963995 -1.35194549133002 0,36.7603337106913 -1.35236395032121 0)
LINESTRING Z (36.7636846570309 -1.36223224500122 0,36.7624931584252 -1.3609281124923 0) | [5 empty] | -1 | 0 | -1 |  |  | 301685143 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 93 | Langa'Ta | Hardy |  |  | 0.197 | UNKNOWN | LINESTRING Z (36.7636846570309 -1.36223224500122 0,36.7624931584252 -1.3609281124923 0)
LINESTRING Z (36.76591701561 -1.36494782278443 0,36.7649949841971 -1.36363436841892 0) | [5 empty] | -1 | 0 | -1 |  |  | 301601927 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 94 | 10602010603 | 1060201060301 |  |  | 0.179 | UNKNOWN | LINESTRING Z (36.76591701561 -1.36494782278443 0,36.7649949841971 -1.36363436841892 0)
LINESTRING Z (36.7608369568325 -1.36805173513509 0,36.7575736263158 -1.36825584429273 0) | [5 empty] | -1 | 0 | -1 |  |  | 301003572 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 95 | 10602010602 | 1060201060201 |  |  | 0.364 | UNKNOWN | LINESTRING Z (36.7608369568325 -1.36805173513509 0,36.7575736263158 -1.36825584429273 0)
LINESTRING Z (36.7670765841199 -1.36999879607117 0,36.7673984075653 -1.36823663832402 0) | [5 empty] | -1 | 0 | -1 |  |  | 301003574 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 96 | Langa'Ta | Hardy |  |  | 0.199 | UNKNOWN | LINESTRING Z (36.7670765841199 -1.36999879607117 0,36.7673984075653 -1.36823663832402 0)
LINESTRING Z (36.7623921963995 -1.35194549133002 0,36.763036432869 -1.35049720568309 0) | NLGLS127 |  |  |  |  | -1 | 0 | -1 |  |  | 301003494 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 97 | 10602010602 | 1060201060202 |  |  | 0.176 | UNKNOWN | LINESTRING Z (36.7623921963995 -1.35194549133002 0,36.763036432869 -1.35049720568309 0)
LINESTRING Z (36.7622855261742 -1.36069603276204 0,36.7609651864401 -1.36078082293381 0) | [5 empty] | -1 | 0 | -1 |  |  | 301687266 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 98 | Langa'Ta | Hardy |  |  | 0.147 | UNKNOWN | LINESTRING Z (36.7622855261742 -1.36069603276204 0,36.7609651864401 -1.36078082293381 0)
LINESTRING Z (36.763036432869 -1.35049720568309 0,36.7644539464403 -1.3479635865548 0,36.7651574651075 -1.34656776213099 0) | NLGLS126 |  |  |  |  | -1 | 0 | -1 |  |  | 301003491 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 99 | 10602010602 | 1060201060202 |  |  | 0.497 | UNKNOWN | LINESTRING Z (36.763036432869 -1.35049720568309 0,36.7644539464403 -1.3479635865548 0,36.7651574651075 -1.34656776213099 0)
LINESTRING Z (36.7667231620065 -1.38047793835761 0,36.7698813824731 -1.38001194403103 0) | [5 empty] | -1 | 0 | -1 |  |  | 301003585 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 100 | 10602010602 | 1060201060201 |  |  | 0.355 | UNKNOWN | LINESTRING Z (36.7667231620065 -1.38047793835761 0,36.7698813824731 -1.38001194403103 0)
LINESTRING Z (36.7618156185011 -1.35592046277368 0,36.7620971077276 -1.35668690737419 0) | NLGLS141 |  |  |  |  | -1 | 0 | -1 |  |  | 301003529 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 101 | Langa'Ta | Hardy |  |  | 0.091 | UNKNOWN | LINESTRING Z (36.7618156185011 -1.35592046277368 0,36.7620971077276 -1.35668690737419 0)
LINESTRING Z (36.7670765841199 -1.36999879607117 0,36.7661985846384 -1.37000010459701 0) | [5 empty] | -1 | 0 | -1 |  |  | 301661325 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 102 | 10602010602 | 1060201060201 |  |  | 0.098 | UNKNOWN | LINESTRING Z (36.7670765841199 -1.36999879607117 0,36.7661985846384 -1.37000010459701 0)
LINESTRING Z (36.7681820421319 -1.37197221229169 0,36.7670765841199 -1.36999879607117 0) | [5 empty] | -1 | 0 | -1 |  |  | 301003575 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 103 | 10602010602 | 1060201060201 |  |  | 0.252 | UNKNOWN | LINESTRING Z (36.7681820421319 -1.37197221229169 0,36.7670765841199 -1.36999879607117 0)
LINESTRING Z (36.7649949841971 -1.36363436841892 0,36.7646794846246 -1.36330388643667 0) | [5 empty] | -1 | 0 | -1 |  |  | 301913662 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 104 | 10602010603 | 1060201060301 |  |  | 0.051 | UNKNOWN | LINESTRING Z (36.7649949841971 -1.36363436841892 0,36.7646794846246 -1.36330388643667 0)
LINESTRING Z (36.7646794846246 -1.36330388643667 0,36.7636846570309 -1.36223224500122 0) | [5 empty] | -1 | 0 | -1 |  |  | 301003542 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 105 | 10602010603 | 1060201060301 |  |  | 0.163 | UNKNOWN | LINESTRING Z (36.7646794846246 -1.36330388643667 0,36.7636846570309 -1.36223224500122 0)
LINESTRING Z (36.7558333036587 -1.36313160563965 0,36.7552123181797 -1.3632251871156 0) | [5 empty] | -1 | 0 | -1 |  |  | 301680868 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 106 | 10602010602 | 1060201060201 |  |  | 0.07 |  | LINESTRING Z (36.7558333036587 -1.36313160563965 0,36.7552123181797 -1.3632251871156 0)
LINESTRING Z (36.757888759798 -1.37319733022595 0,36.7579264893446 -1.37349144029173 0) | KLGLS076 |  |  |  |  | -1 | 0 | -1 |  |  | 301004272 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 107 | 10602010602 | 1060201060201 |  |  | 0.033 | UNKNOWN | LINESTRING Z (36.757888759798 -1.37319733022595 0,36.7579264893446 -1.37349144029173 0)
LINESTRING Z (36.7462733180924 -1.37453872997444 0,36.7411357236897 -1.3751567511646 0) | KLGLS068 |  |  |  |  | -1 | 0 | -1 |  |  | 301004255 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 108 | Langa'Ta | Hardy |  |  | 0.576 | UNKNOWN | LINESTRING Z (36.7462733180924 -1.37453872997444 0,36.7411357236897 -1.3751567511646 0)
LINESTRING Z (36.7462733180924 -1.37453872997444 0) | KLGLS069 |  |  |  |  | -1 | 0 | -1 |  |  | 301913144 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 109 | Langa'Ta | Hardy |  |  | 0 | UNKNOWN | LINESTRING Z (36.7462733180924 -1.37453872997444 0)
LINESTRING Z (36.7411357236897 -1.3751567511646 0,36.7410896562047 -1.37418876869938 0) | [5 empty] | -1 | 0 | -1 |  |  | 301683747 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 110 | Langa'Ta | Hardy |  |  | 0.108 | UNKNOWN | LINESTRING Z (36.7411357236897 -1.3751567511646 0,36.7410896562047 -1.37418876869938 0)
LINESTRING Z (36.7411357236897 -1.3751567511646 0,36.7412361387439 -1.37728738234144 0) | KLGLS068 |  |  |  |  | -1 | 0 | -1 |  |  | 301683746 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 111 | Langa'Ta | Hardy |  |  | 0.237 | UNKNOWN | LINESTRING Z (36.7411357236897 -1.3751567511646 0,36.7412361387439 -1.37728738234144 0)
LINESTRING Z (36.7605795763563 -1.35286426923963 0,36.7603337106913 -1.35236395032121 0) | NLGLS129 |  |  |  |  | -1 | 0 | -1 |  |  | 301966753 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 112 | Langa'Ta | Langa'Ta |  |  | 0.062 | UNKNOWN | LINESTRING Z (36.7605795763563 -1.35286426923963 0,36.7603337106913 -1.35236395032121 0)
LINESTRING Z (36.7603337106913 -1.35236395032121 0,36.7589102901439 -1.35254987804557 0) | NLGLS129 |  |  |  |  | -1 | 0 | -1 |  |  | 301003500 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 113 | Langa'Ta | Langa'Ta |  |  | 0.16 | UNKNOWN | LINESTRING Z (36.7603337106913 -1.35236395032121 0,36.7589102901439 -1.35254987804557 0)
LINESTRING Z (36.7462733180924 -1.37453872997444 0,36.7463050284598 -1.38080303707381 0,36.7471553579504 -1.38099637926356 0) | KLGLS070 |  |  |  |  | -1 | 0 | -1 |  |  | 301004258 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 114 | Langa'Ta | Hardy |  |  | 0.794 | UNKNOWN | LINESTRING Z (36.7462733180924 -1.37453872997444 0,36.7463050284598 -1.38080303707381 0,36.7471553579504 -1.38099637926356 0)
LINESTRING Z (36.7552123181797 -1.3632251871156 0) | [5 empty] | -1 | 0 | -1 |  |  | 301913123 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 115 | 10602010602 | 1060201060201 |  |  | 0 | UNKNOWN | LINESTRING Z (36.7552123181797 -1.3632251871156 0)
LINESTRING Z (36.7569132002294 -1.35272869876763 0,36.7569132002294 -1.35272869876763 0) | NLGLS132 |  |  |  |  | -1 | 0 | -1 |  |  | 301003510 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 116 | 10602010602 | 1060201060202 |  |  | 0 | UNKNOWN | LINESTRING Z (36.7569132002294 -1.35272869876763 0,36.7569132002294 -1.35272869876763 0)
LINESTRING Z (36.7563236410844 -1.35075336316955 0) | [5 empty] | -1 | 0 | -1 |  |  | 301685132 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 117 | 10602010602 | 1060201060202 |  |  | 0 | UNKNOWN | LINESTRING Z (36.7563236410844 -1.35075336316955 0)
LINESTRING Z (36.7589102901439 -1.35254987804557 0,36.7586187095724 -1.35002870712677 0,36.7586065662688 -1.3493365388204 0,36.7586495558373 -1.34867344535816 0) | NLGLS130 |  |  |  |  | -1 | 0 | -1 |  |  | 301003506 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 118 | 10602010602 | 1060201060202 |  |  | 0.434 | UNKNOWN | LINESTRING Z (36.7589102901439 -1.35254987804557 0,36.7586187095724 -1.35002870712677 0,36.7586065662688 -1.3493365388204 0,36.7586495558373 -1.34867344535816 0)
LINESTRING Z (36.7563878830746 -1.35283104378804 0,36.756256521237 -1.35172476577396 0) | NLGLS134 |  |  |  |  | -1 | 0 | -1 |  |  | 301003514 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 119 | 10602010602 | 1060201060202 |  |  | 0.124 | UNKNOWN | LINESTRING Z (36.7563878830746 -1.35283104378804 0,36.756256521237 -1.35172476577396 0)
LINESTRING Z (36.7569132002294 -1.35272869876763 0,36.7563878830746 -1.35283104378804 0) | NLGLS133 |  |  |  |  | -1 | 0 | -1 |  |  | 301003513 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 120 | 10602010602 | 1060201060202 |  |  | 0.06 | UNKNOWN | LINESTRING Z (36.7569132002294 -1.35272869876763 0,36.7563878830746 -1.35283104378804 0)
LINESTRING Z (36.7503475000925 -1.35358701297463 0,36.7503475000925 -1.35358701297463 0) | NLGLS138 |  |  |  |  | -1 | 0 | -1 |  |  | 301003520 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 121 | 10602010602 | 1060201060202 |  |  | 0 | UNKNOWN | LINESTRING Z (36.7503475000925 -1.35358701297463 0,36.7503475000925 -1.35358701297463 0)
LINESTRING Z (36.7531188035318 -1.35326474608744 0,36.7503475000925 -1.35358701297463 0) | NLGLS137 |  |  |  |  | -1 | 0 | -1 |  |  | 301003517 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 122 | 10602010602 | 1060201060202 |  |  | 0.311 | UNKNOWN | LINESTRING Z (36.7531188035318 -1.35326474608744 0,36.7503475000925 -1.35358701297463 0)
LINESTRING Z (36.7568232402855 -1.34692593186729 0,36.7539687234416 -1.34724283485521 0) | KLGLS102 |  |  |  |  | -1 | 0 | -1 |  |  | 301685123 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 123 | 10602010602 | 1060201060202 |  |  | 0.32 | UNKNOWN | LINESTRING Z (36.7568232402855 -1.34692593186729 0,36.7539687234416 -1.34724283485521 0)
LINESTRING Z (36.7594311309821 -1.36389019607431 0,36.7558333036587 -1.36313160563965 0) | [5 empty] | -1 | 0 | -1 |  |  | 301003540 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 124 | Langa'Ta | Hardy |  |  | 0.409 | UNKNOWN | LINESTRING Z (36.7594311309821 -1.36389019607431 0,36.7558333036587 -1.36313160563965 0)
LINESTRING Z (36.7548357734722 -1.35305642471318 0,36.7531188035318 -1.35326474608744 0) | NLGLS136 |  |  |  |  | -1 | 0 | -1 |  |  | 301003516 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 125 | 10602010602 | 1060201060202 |  |  | 0.193 | UNKNOWN | LINESTRING Z (36.7548357734722 -1.35305642471318 0,36.7531188035318 -1.35326474608744 0)
LINESTRING Z (36.7579665525604 -1.34209999724138 0) | [5 empty] | -1 | 0 | -1 |  |  | 301678128 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 126 | 10602010602 | 1060201060202 |  |  | 0 | UNKNOWN | LINESTRING Z (36.7579665525604 -1.34209999724138 0)
LINESTRING Z (36.7618227067845 -1.36177241961839 0,36.7594311309821 -1.36389019607431 0) | [5 empty] | -1 | 0 | -1 |  |  | 301003538 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 127 | 10602010602 | 1060201060201 |  |  | 0.356 | 10024:1 | LINESTRING Z (36.7618227067845 -1.36177241961839 0,36.7594311309821 -1.36389019607431 0)
LINESTRING Z (36.7563878830746 -1.35283104378804 0,36.7548357734722 -1.35305642471318 0) | NLGLS135 |  |  |  |  | -1 | 0 | -1 |  |  | 301003515 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 128 | 10602010602 | 1060201060202 |  |  | 0.175 | UNKNOWN | LINESTRING Z (36.7563878830746 -1.35283104378804 0,36.7548357734722 -1.35305642471318 0)
LINESTRING Z (36.7624223632652 -1.37265521504387 0,36.7681820421319 -1.37197221229169 0) | KLGLS075 |  |  |  |  | -1 | 0 | -1 |  |  | 301004270 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 129 | 10602010602 | 1060201060201 |  |  | 0.646 | UNKNOWN | LINESTRING Z (36.7624223632652 -1.37265521504387 0,36.7681820421319 -1.37197221229169 0)
LINESTRING Z (36.7646794846246 -1.36330388643667 0,36.7646794846246 -1.36330388643667 0) | [5 empty] | -1 | 0 | -1 |  |  | 301913663 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 130 | Mugumoini | Bomas |  |  | 0 |  | LINESTRING Z (36.7646794846246 -1.36330388643667 0,36.7646794846246 -1.36330388643667 0)
LINESTRING Z (36.7555190442461 -1.35702584112019 0,36.7554608025107 -1.35688558713458 0) | [5 empty] | -1 | 0 | -1 |  |  | 30755 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 131 | Langa'Ta | Hardy |  |  | 0.017 |  | LINESTRING Z (36.7555190442461 -1.35702584112019 0,36.7554608025107 -1.35688558713458 0)
LINESTRING Z (36.7617961576617 -1.35583823096373 0,36.7623921963995 -1.35194549133002 0) | NLGLS140 |  |  |  |  | -1 | 0 | -1 |  |  | 301913116 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 132 | Langa'Ta | Langa'Ta |  |  | 0.438 |  | LINESTRING Z (36.7617961576617 -1.35583823096373 0,36.7623921963995 -1.35194549133002 0)
LINESTRING Z (36.7471553579504 -1.38099637926356 0,36.7463050284598 -1.38080303707381 0,36.7463032038169 -1.38080988757234 0) | KLGLS071 |  |  |  |  | -1 | 0 | -1 |  |  | 301004260 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 133 | Langa'Ta | Hardy |  |  | 0.098 | UNKNOWN | LINESTRING Z (36.7471553579504 -1.38099637926356 0,36.7463050284598 -1.38080303707381 0,36.7463032038169 -1.38080988757234 0)
LINESTRING Z (36.7603337106913 -1.35236395032121 0,36.7605795763563 -1.35286426923963 0) | [5 empty] | -1 | 0 | -1 |  |  | 30758 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 134 | Langa'Ta | Langa'Ta |  |  | 0.062 | UNKNOWN | LINESTRING Z (36.7603337106913 -1.35236395032121 0,36.7605795763563 -1.35286426923963 0)
LINESTRING Z (36.7617961576617 -1.35583823096373 0,36.7609729925618 -1.3559546392936 0,36.7584725839617 -1.35639817290244 0) | [5 empty] | -1 | 0 | -1 |  |  | 301661352 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 135 | Langa'Ta | Hardy |  |  | 0.375 | UNKNOWN | LINESTRING Z (36.7617961576617 -1.35583823096373 0,36.7609729925618 -1.3559546392936 0,36.7584725839617 -1.35639817290244 0)
LINESTRING Z (36.7584725839617 -1.35639817290244 0,36.7584725839617 -1.35639817290244 0) | [5 empty] | -1 | 0 | -1 |  |  | 30748 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 136 | Langa'Ta | Hardy |  |  | 0 |  | LINESTRING Z (36.7584725839617 -1.35639817290244 0,36.7584725839617 -1.35639817290244 0)
LINESTRING Z (36.7624322359531 -1.35891324510337 0,36.7616372656626 -1.35898377956509 0) | [5 empty] | -1 | 0 | -1 |  |  | 301686584 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 137 | Langa'Ta | Hardy |  |  | 0.089 | UNKNOWN | LINESTRING Z (36.7624322359531 -1.35891324510337 0,36.7616372656626 -1.35898377956509 0)
LINESTRING Z (36.7646794846246 -1.36330388643667 0,36.7645527914373 -1.36342505805443 0) | [5 empty] | -1 | 0 | -1 |  |  | 301948063 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 138 | Mugumoini | Bomas |  |  | 0.02 |  | LINESTRING Z (36.7646794846246 -1.36330388643667 0,36.7645527914373 -1.36342505805443 0)
LINESTRING Z (36.7555190442461 -1.35702584112019 0,36.7584725839617 -1.35639817290244 0,36.7555190442461 -1.35702584112019 0) | [5 empty] | -1 | 0 | -1 |  |  | 301948112 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 139 | Langa'Ta | Hardy |  |  | 0.672 | UNKNOWN | LINESTRING Z (36.7555190442461 -1.35702584112019 0,36.7584725839617 -1.35639817290244 0,36.7555190442461 -1.35702584112019 0)
LINESTRING Z (36.7554793265145 -1.3571046954011 0,36.7555190442461 -1.35702584112019 0) | [5 empty] | -1 | 0 | -1 |  |  | 301948113 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 140 | Langa'Ta | Hardy |  |  | 0.01 | UNKNOWN | LINESTRING Z (36.7554793265145 -1.3571046954011 0,36.7555190442461 -1.35702584112019 0)
LINESTRING Z (36.7612068626399 -1.37964570579744 0,36.7612166137447 -1.38256040644122 0,36.7612165638942 -1.38254550565052 0) | KLGLS082 |  |  |  |  | -1 | 0 | -1 |  |  | 301004286 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 141 | Langa'Ta | Hardy |  |  | 0.326 | UNKNOWN | LINESTRING Z (36.7612068626399 -1.37964570579744 0,36.7612166137447 -1.38256040644122 0,36.7612165638942 -1.38254550565052 0)
LINESTRING Z (36.7567865754473 -1.37905058253932 0,36.7567183085312 -1.38099466561844 0) | [5 empty] | -1 | 0 | -1 |  |  | 301679146 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 142 | Langa'Ta | Hardy |  |  | 0.217 | UNKNOWN | LINESTRING Z (36.7567865754473 -1.37905058253932 0,36.7567183085312 -1.38099466561844 0)
LINESTRING Z (36.7616185428589 -1.35672560455267 0,36.7620971077276 -1.35668690737419 0) | [5 empty] | -1 | 0 | -1 |  |  | 301719075 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 143 | Langa'Ta | Hardy |  |  | 0.053 |  | LINESTRING Z (36.7616185428589 -1.35672560455267 0,36.7620971077276 -1.35668690737419 0)
LINESTRING Z (36.7585500007543 -1.3788663993872 0,36.7567865754473 -1.37905058253932 0) | KLGLS085 |  |  |  |  | -1 | 0 | -1 |  |  | 301004293 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 144 | Langa'Ta | Hardy |  |  | 0.197 | UNKNOWN | LINESTRING Z (36.7585500007543 -1.3788663993872 0,36.7567865754473 -1.37905058253932 0)
LINESTRING Z (36.7624931584252 -1.3609281124923 0,36.7618227067845 -1.36177241961839 0) | [5 empty] | -1 | 0 | -1 |  |  | 301003535 | hardy MV LINE SECTION | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=MV LINE SECTION | 145 | Langa'Ta | Hardy |  |  | 0.12 | 10024:1 | LINESTRING Z (36.7624931584252 -1.3609281124923 0,36.7618227067845 -1.36177241961839 0)
LINESTRING Z (36.7579665525604 -1.34209999724138 0,36.7579665525604 -1.34209999724138 0) | HARDY EX LANGATA |  |  |  |  | -1 | 0 | -1 |  |  | 205601198 | hardy PRIMARY CIRCUIT BREAKER | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=PRIMARY CIRCUIT BREAKER | 146 | Langa'Ta | Langa'Ta |  |  | 0 |  | LINESTRING Z (36.7579665525604 -1.34209999724138 0,36.7579665525604 -1.34209999724138 0) | 205601198
LINESTRING Z (36.7552123181797 -1.3632251871156 0,36.7552123181797 -1.3632251871156 0) | Y5254 |  |  |  |  | -1 | 0 | -1 |  |  | 303616820 | hardy SECONDARY SWITCH ISOLATOR | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY SWITCH ISOLATOR | 147 | Langa'Ta | Hardy |  |  | 0 |  | LINESTRING Z (36.7552123181797 -1.3632251871156 0,36.7552123181797 -1.3632251871156 0) |  | Y5254 | UNKNOWN
LINESTRING Z (36.7565940277503 -1.36136318895282 0,36.7565940277503 -1.36136318895282 0) | Y5278 |  |  |  |  | -1 | 0 | -1 |  |  | 303616821 | hardy SECONDARY SWITCH ISOLATOR | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY SWITCH ISOLATOR | 148 | Langa'Ta | Hardy |  |  | 0 |  | LINESTRING Z (36.7565940277503 -1.36136318895282 0,36.7565940277503 -1.36136318895282 0) |  | Y5278 | UNKNOWN
LINESTRING Z (36.7471094242747 -1.35713395967179 0,36.7471094242747 -1.35713395967179 0) | FAUL THROWER |  |  |  |  | -1 | 0 | -1 |  |  | 303001945 | hardy SECONDARY SWITCH ISOLATOR | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY SWITCH ISOLATOR | 149 | Langa'Ta | Hardy |  |  | 0 |  | LINESTRING Z (36.7471094242747 -1.35713395967179 0,36.7471094242747 -1.35713395967179 0) |  | FAUL THROWER | UNKNOWN
LINESTRING Z (36.7471094242747 -1.35713395967179 0,36.7471094242747 -1.35713395967179 0) | OD N.O. |  |  |  |  | -1 | 0 | -1 |  |  | 303001955 | hardy SECONDARY SWITCH ISOLATOR | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY SWITCH ISOLATOR | 150 | Langa'Ta | Hardy |  |  | 0 |  | LINESTRING Z (36.7471094242747 -1.35713395967179 0,36.7471094242747 -1.35713395967179 0) |  | OD N.O. | UNKNOWN
LINESTRING Z (36.7471094242747 -1.35713395967179 0,36.7471094242747 -1.35713395967179 0) | SWITCH |  |  |  |  | -1 | 0 | -1 |  |  | 303001947 | hardy SECONDARY SWITCH ISOLATOR | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY SWITCH ISOLATOR | 151 | Langa'Ta | Hardy |  |  | 0 |  | LINESTRING Z (36.7471094242747 -1.35713395967179 0,36.7471094242747 -1.35713395967179 0) |  | SWITCH | UNKNOWN
LINESTRING Z (36.7620971077276 -1.35668690737419 0,36.7620971077276 -1.35668690737419 0) | Y113 |  |  |  |  | -1 | 0 | -1 |  |  | 303000978 | hardy SECONDARY SWITCH ISOLATOR | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY SWITCH ISOLATOR | 152 | Langa'Ta | Hardy |  |  | 0 |  | LINESTRING Z (36.7620971077276 -1.35668690737419 0,36.7620971077276 -1.35668690737419 0) |  | Y113 | UNKNOWN
LINESTRING Z (36.7617961576617 -1.35583823096373 0,36.7617961576617 -1.35583823096373 0) | AY113 |  |  |  |  | -1 | 0 | -1 |  |  | 303616816 | hardy SECONDARY SWITCH ISOLATOR | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY SWITCH ISOLATOR | 153 | Langa'Ta | Hardy |  |  | 0 |  | LINESTRING Z (36.7617961576617 -1.35583823096373 0,36.7617961576617 -1.35583823096373 0) |  | AY113 | 10027:6
LINESTRING Z (36.7569132002294 -1.35272869876763 0,36.7569132002294 -1.35272869876763 0) | AY1104 |  |  |  |  | -1 | 0 | -1 |  |  | 303608991 | hardy SECONDARY SWITCH ISOLATOR | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY SWITCH ISOLATOR | 154 | Langa'Ta | Langa'Ta |  |  | 0 |  | LINESTRING Z (36.7569132002294 -1.35272869876763 0,36.7569132002294 -1.35272869876763 0) |  | AY1104 | UNKNOWN
LINESTRING Z (36.756256521237 -1.35172476577396 0,36.756256521237 -1.35172476577396 0) | Y1104 |  |  |  |  | -1 | 0 | -1 |  |  | 303608990 | hardy SECONDARY SWITCH ISOLATOR | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY SWITCH ISOLATOR | 155 | Langa'Ta | Langa'Ta |  |  | 0 |  | LINESTRING Z (36.756256521237 -1.35172476577396 0,36.756256521237 -1.35172476577396 0) |  | Y1104 | UNKNOWN
LINESTRING Z (36.7563236410844 -1.35075336316955 0,36.7563236410844 -1.35075336316955 0) | SWITCH |  |  |  |  | -1 | 0 | -1 |  |  | 303608988 | hardy SECONDARY SWITCH ISOLATOR | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY SWITCH ISOLATOR | 156 | Langa'Ta | Langa'Ta |  |  | 0 |  | LINESTRING Z (36.7563236410844 -1.35075336316955 0,36.7563236410844 -1.35075336316955 0) |  | SWITCH | UNKNOWN
LINESTRING Z (36.7563236410844 -1.35075336316955 0,36.7563236410844 -1.35075336316955 0) | L.B.S |  |  |  |  | -1 | 0 | -1 |  |  | 303608992 | hardy SECONDARY SWITCH ISOLATOR | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY SWITCH ISOLATOR | 157 | Langa'Ta | Langa'Ta |  |  | 0 |  | LINESTRING Z (36.7563236410844 -1.35075336316955 0,36.7563236410844 -1.35075336316955 0) |  | L.B.S | UNKNOWN
LINESTRING Z (36.757891416378 -1.3499707011205 0,36.757891416378 -1.3499707011205 0) | SWITCH |  |  |  |  | -1 | 0 | -1 |  |  | 303608987 | hardy SECONDARY SWITCH ISOLATOR | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY SWITCH ISOLATOR | 158 | Langa'Ta | Langa'Ta |  |  | 0 |  | LINESTRING Z (36.757891416378 -1.3499707011205 0,36.757891416378 -1.3499707011205 0) |  | SWITCH | UNKNOWN
LINESTRING Z (36.7654302091879 -1.34598825744552 0,36.7654302091879 -1.34598825744552 0) | AY101 |  |  |  |  | -1 | 0 | -1 |  |  | 303000975 | hardy SECONDARY SWITCH ISOLATOR | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY SWITCH ISOLATOR | 159 | Langa'Ta | Langa'Ta |  |  | 0 |  | LINESTRING Z (36.7654302091879 -1.34598825744552 0,36.7654302091879 -1.34598825744552 0) |  | AY101 | 10027:6
LINESTRING Z (36.7654302091879 -1.34598825744552 0,36.7654302091879 -1.34598825744552 0) | Y101 |  |  |  |  | -1 | 0 | -1 |  |  | 303611023 | hardy SECONDARY SWITCH ISOLATOR | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY SWITCH ISOLATOR | 160 | Langa'Ta | Langa'Ta |  |  | 0 |  | LINESTRING Z (36.7654302091879 -1.34598825744552 0,36.7654302091879 -1.34598825744552 0) |  | Y101 | UNKNOWN
LINESTRING Z (36.7579665525604 -1.34209999724138 0,36.7579665525604 -1.34209999724138 0) | Y5176 |  |  |  |  | -1 | 0 | -1 |  |  | 303610279 | hardy SECONDARY SWITCH ISOLATOR | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY SWITCH ISOLATOR | 161 | Langa'Ta | Langa'Ta |  |  | 0 |  | LINESTRING Z (36.7579665525604 -1.34209999724138 0,36.7579665525604 -1.34209999724138 0) |  | Y5176 | UNKNOWN
LINESTRING Z (36.7462733180924 -1.37453872997444 0,36.7462733180924 -1.37453872997444 0) | Y5138 |  |  |  |  | -1 | 0 | -1 |  |  | 303001271 | hardy SECONDARY SWITCH ISOLATOR | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY SWITCH ISOLATOR | 162 | Langa'Ta | Hardy |  |  | 0 |  | LINESTRING Z (36.7462733180924 -1.37453872997444 0,36.7462733180924 -1.37453872997444 0) |  | Y5138 | UNKNOWN
LINESTRING Z (36.7462733180924 -1.37453872997444 0,36.7462733180924 -1.37453872997444 0) | Y1118 |  |  |  |  | -1 | 0 | -1 |  |  | 303001272 | hardy SECONDARY SWITCH ISOLATOR | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY SWITCH ISOLATOR | 163 | Langa'Ta | Hardy |  |  | 0 |  | LINESTRING Z (36.7462733180924 -1.37453872997444 0,36.7462733180924 -1.37453872997444 0) |  | Y1118
LINESTRING Z (36.7667231620065 -1.38047793835761 0,36.7667231620065 -1.38047793835761 0) | Y171 |  |  |  |  | -1 | 0 | -1 |  |  | 303001020 | hardy SECONDARY SWITCH ISOLATOR | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY SWITCH ISOLATOR | 164 | Langa'Ta | Hardy |  |  | 0 |  | LINESTRING Z (36.7667231620065 -1.38047793835761 0,36.7667231620065 -1.38047793835761 0) |  | Y171 | UNKNOWN
LINESTRING Z (36.7681820421319 -1.37197221229169 0,36.7681820421319 -1.37197221229169 0) | Y118 |  |  |  |  | -1 | 0 | -1 |  |  | 303001017 | hardy SECONDARY SWITCH ISOLATOR | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY SWITCH ISOLATOR | 165 | Langa'Ta | Hardy |  |  | 0 |  | LINESTRING Z (36.7681820421319 -1.37197221229169 0,36.7681820421319 -1.37197221229169 0) |  | Y118 | UNKNOWN
LINESTRING Z (36.7681820421319 -1.37197221229169 0,36.7681820421319 -1.37197221229169 0) | Y146 |  |  |  |  | -1 | 0 | -1 |  |  | 303000983 | hardy SECONDARY SWITCH ISOLATOR | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY SWITCH ISOLATOR | 166 | Langa'Ta | Hardy |  |  | 0 |  | LINESTRING Z (36.7681820421319 -1.37197221229169 0,36.7681820421319 -1.37197221229169 0) |  | Y146 | UNKNOWN
LINESTRING Z (36.7698813824731 -1.38001194403103 0,36.7698813824731 -1.38001194403103 0) | Y172 |  |  |  |  | -1 | 0 | -1 |  |  | 303004094 | hardy SECONDARY SWITCH ISOLATOR | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY SWITCH ISOLATOR | 167 | Langa'Ta | Hardy |  |  | 0 |  | LINESTRING Z (36.7698813824731 -1.38001194403103 0,36.7698813824731 -1.38001194403103 0) |  | Y172 | UNKNOWN
LINESTRING Z (36.7609651864401 -1.36078082293381 0,36.7609651864401 -1.36078082293381 0) | [5 empty] | -1 | 0 | -1 |  |  | 312627135 | hardy SECONDARY TAPLIN | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY TAPLIN | 168 | Langa'Ta | Hardy |  | 312627135 | 0 |  | LINESTRING Z (36.7609651864401 -1.36078082293381 0,36.7609651864401 -1.36078082293381 0) |  |  |  | TP018
LINESTRING Z (36.768206929511 -1.37629011528426 0,36.768206929511 -1.37629011528426 0) | [5 empty] | -1 | 0 | -1 |  |  | 312000447 | hardy SECONDARY TAPLIN | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY TAPLIN | 169 | Langa'Ta | Hardy |  | 312000447 | 0 |  | LINESTRING Z (36.768206929511 -1.37629011528426 0,36.768206929511 -1.37629011528426 0) |  |  |  | TP017
LINESTRING Z (36.7584725839617 -1.35639817290244 0,36.7584725839617 -1.35639817290244 0) | [5 empty] | -1 | 0 | -1 |  |  | 312620396 | hardy SECONDARY TAPLIN | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY TAPLIN | 170 | Langa'Ta | Hardy |  | 312620396 | 0 |  | LINESTRING Z (36.7584725839617 -1.35639817290244 0,36.7584725839617 -1.35639817290244 0) |  |  |  | TP006
LINESTRING Z (36.7410896562047 -1.37418876869938 0,36.7410896562047 -1.37418876869938 0) | [5 empty] | -1 | 0 | -1 |  |  | 312619735 | hardy SECONDARY TAPLIN | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY TAPLIN | 171 | Langa'Ta | Hardy |  | 312619735 | 0 |  | LINESTRING Z (36.7410896562047 -1.37418876869938 0,36.7410896562047 -1.37418876869938 0) |  |  |  | TP026
LINESTRING Z (36.7412361387439 -1.37728738234144 0,36.7412361387439 -1.37728738234144 0) | [5 empty] | -1 | 0 | -1 |  |  | 312000609 | hardy SECONDARY TAPLIN | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY TAPLIN | 172 | Langa'Ta | Hardy |  | 312000609 | 0 |  | LINESTRING Z (36.7412361387439 -1.37728738234144 0,36.7412361387439 -1.37728738234144 0) |  |  |  | TP027
LINESTRING Z (36.7646794846246 -1.36330388643667 0,36.7646794846246 -1.36330388643667 0) | [5 empty] | -1 | 0 | -1 |  |  | 312648409 | hardy SECONDARY TAPLIN | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY TAPLIN | 173 | Mugumoini | Bomas |  | 312648409 | 0 |  | LINESTRING Z (36.7646794846246 -1.36330388643667 0,36.7646794846246 -1.36330388643667 0)
LINESTRING Z (36.7586892630442 -1.38004691996939 0,36.7586892630442 -1.38004691996939 0) | [5 empty] | -1 | 0 | -1 |  |  | 312621935 | hardy SECONDARY TAPLIN | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY TAPLIN | 174 | Langa'Ta | Hardy |  | 312621935 | 0 |  | LINESTRING Z (36.7586892630442 -1.38004691996939 0,36.7586892630442 -1.38004691996939 0) |  |  |  | TP033
LINESTRING Z (36.7552123181797 -1.3632251871156 0,36.7552123181797 -1.3632251871156 0) | [5 empty] | -1 | 0 | -1 |  |  | 312000422 | hardy SECONDARY TAPLIN | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY TAPLIN | 175 | Langa'Ta | Hardy |  | 312000422 | 0 |  | LINESTRING Z (36.7552123181797 -1.3632251871156 0,36.7552123181797 -1.3632251871156 0) |  |  |  | TP009
LINESTRING Z (36.7636846570309 -1.36223224500122 0,36.7637952838629 -1.36213885472542 0) | [5 empty] | -1 | 0 | -1 |  |  | 312620373 | hardy SECONDARY TAPLIN | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY TAPLIN | 176 | Mugumoini | Bomas |  | 312620373 | 0.016 |  | LINESTRING Z (36.7636846570309 -1.36223224500122 0,36.7637952838629 -1.36213885472542 0) |  |  |  | TP010
LINESTRING Z (36.7673305364644 -1.36377539781515 0,36.7673305364644 -1.36377539781515 0) | [5 empty] | -1 | 0 | -1 |  |  | 312625620 | hardy SECONDARY TAPLIN | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY TAPLIN | 177 | Mugumoini | Bomas |  | 312625620 | 0 |  | LINESTRING Z (36.7673305364644 -1.36377539781515 0,36.7673305364644 -1.36377539781515 0) |  |  |  | TP011
LINESTRING Z (36.7618156185011 -1.35592046277368 0,36.7618156185011 -1.35592046277368 0) | TP067 |  |  |  |  | -1 | 0 | -1 |  |  | 312000418 | hardy SECONDARY TAPLIN | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY TAPLIN | 178 | Langa'Ta | Hardy |  | 312000418 | 0 |  | LINESTRING Z (36.7618156185011 -1.35592046277368 0,36.7618156185011 -1.35592046277368 0) |  |  |  | TP007
LINESTRING Z (36.7575736263158 -1.36825584429273 0,36.7575736263158 -1.36825584429273 0) | [5 empty] | -1 | 0 | -1 |  |  | 312000427 | hardy SECONDARY TAPLIN | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY TAPLIN | 179 | Langa'Ta | Hardy |  | 312000427 | 0 |  | LINESTRING Z (36.7575736263158 -1.36825584429273 0,36.7575736263158 -1.36825584429273 0) |  |  |  | TP015
LINESTRING Z (36.7569132002294 -1.35272869876763 0,36.7569132002294 -1.35272869876763 0) | TP061 |  |  |  |  | -1 | 0 | -1 |  |  | 312000410 | hardy SECONDARY TAPLIN | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY TAPLIN | 180 | Langa'Ta | Langa'Ta |  | 312000410 | 0 |  | LINESTRING Z (36.7569132002294 -1.35272869876763 0,36.7569132002294 -1.35272869876763 0) |  |  |  | TP004
LINESTRING Z (36.7633226633752 -1.34656625225938 0,36.7633226633752 -1.34656625225938 0) | TP057 |  |  |  |  | -1 | 0 | -1 |  |  | 312000401 | hardy SECONDARY TAPLIN | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY TAPLIN | 181 | Langa'Ta | Langa'Ta |  | 312000401 | 0 |  | LINESTRING Z (36.7633226633752 -1.34656625225938 0,36.7633226633752 -1.34656625225938 0) |  |  |  | TP006
LINESTRING Z (36.7503475000925 -1.35358701297463 0,36.7503475000925 -1.35358701297463 0) | TP065 |  |  |  |  | -1 | 0 | -1 |  |  | 312000415 | hardy SECONDARY TAPLIN | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY TAPLIN | 182 | Langa'Ta | Langa'Ta |  | 312000415 | 0 |  | LINESTRING Z (36.7503475000925 -1.35358701297463 0,36.7503475000925 -1.35358701297463 0) |  |  |  | TP003
LINESTRING Z (36.7579264893446 -1.37349144029173 0,36.7579264893446 -1.37349144029173 0) | [5 empty] | -1 | 0 | -1 |  |  | 312000615 | hardy SECONDARY TAPLIN | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY TAPLIN | 183 | Langa'Ta | Hardy |  | 312000615 | 0 |  | LINESTRING Z (36.7579264893446 -1.37349144029173 0,36.7579264893446 -1.37349144029173 0) |  |  |  | TP032
LINESTRING Z (36.7681820421319 -1.37197221229169 0,36.7681820421319 -1.37197221229169 0) | [5 empty] | -1 | 0 | -1 |  |  | 312620380 | hardy SECONDARY TAPLIN | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY TAPLIN | 184 | Mugumoini | Bomas |  | 312620380 | 0 |  | LINESTRING Z (36.7681820421319 -1.37197221229169 0,36.7681820421319 -1.37197221229169 0) |  |  |  | TP016
LINESTRING Z (36.7548357734722 -1.35305642471318 0,36.7548357734722 -1.35305642471318 0) | TP063 |  |  |  |  | -1 | 0 | -1 |  |  | 312000412 | hardy SECONDARY TAPLIN | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY TAPLIN | 185 | Langa'Ta | Langa'Ta |  | 312000412 | 0 |  | LINESTRING Z (36.7548357734722 -1.35305642471318 0,36.7548357734722 -1.35305642471318 0) |  |  |  | TP002
LINESTRING Z (36.7661985846384 -1.37000010459701 0,36.7661985846384 -1.37000010459701 0) | [5 empty] | -1 | 0 | -1 |  |  | 312000444 | hardy SECONDARY TAPLIN | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY TAPLIN | 186 | Langa'Ta | Hardy |  | 312000444 | 0 |  | LINESTRING Z (36.7661985846384 -1.37000010459701 0,36.7661985846384 -1.37000010459701 0) |  |  |  | TP019
LINESTRING Z (36.7608369568325 -1.36805173513509 0,36.7608369568325 -1.36805173513509 0) | [5 empty] | -1 | 0 | -1 |  |  | 312003851 | hardy SECONDARY TAPLIN | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY TAPLIN | 187 | Langa'Ta | Hardy |  | 312003851 | 0 |  | LINESTRING Z (36.7608369568325 -1.36805173513509 0,36.7608369568325 -1.36805173513509 0) |  |  |  | TP014
LINESTRING Z (36.7618227067845 -1.36177241961839 0,36.7618227067845 -1.36177241961839 0) | [5 empty] | -1 | 0 | -1 |  |  | 312000419 | hardy SECONDARY TAPLIN | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY TAPLIN | 188 | Langa'Ta | Hardy |  | 312000419 | 0 |  | LINESTRING Z (36.7618227067845 -1.36177241961839 0,36.7618227067845 -1.36177241961839 0) |  |  |  | TP008
LINESTRING Z (36.7505226572627 -1.37408454262385 0,36.7505226572627 -1.37408454262385 0) | [5 empty] | -1 | 0 | -1 |  |  | 312000613 | hardy SECONDARY TAPLIN | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY TAPLIN | 189 | Langa'Ta | Hardy |  | 312000613 | 0 |  | LINESTRING Z (36.7505226572627 -1.37408454262385 0,36.7505226572627 -1.37408454262385 0) |  |  |  | TP031
LINESTRING Z (36.749047924785 -1.38149034139184 0,36.749047924785 -1.38149034139184 0) | [5 empty] | -1 | 0 | -1 |  |  | 312000612 | hardy SECONDARY TAPLIN | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY TAPLIN | 190 | Langa'Ta | Hardy |  | 312000612 | 0 |  | LINESTRING Z (36.749047924785 -1.38149034139184 0,36.749047924785 -1.38149034139184 0) |  |  |  | TP029
LINESTRING Z (36.7471553579504 -1.38099637926356 0,36.7471553579504 -1.38099637926356 0) | [5 empty] | -1 | 0 | -1 |  |  | 312000610 | hardy SECONDARY TAPLIN | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY TAPLIN | 191 | Langa'Ta | Hardy |  | 312000610 | 0 |  | LINESTRING Z (36.7471553579504 -1.38099637926356 0,36.7471553579504 -1.38099637926356 0) |  |  |  | TP028
LINESTRING Z (36.7644866512733 -1.37824857283834 0,36.7644866512733 -1.37824857283834 0) | [5 empty] | -1 | 0 | -1 |  |  | 312000620 | hardy SECONDARY TAPLIN | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY TAPLIN | 192 | Langa'Ta | Hardy |  | 312000620 | 0 |  | LINESTRING Z (36.7644866512733 -1.37824857283834 0,36.7644866512733 -1.37824857283834 0) |  |  |  | TP034
LINESTRING Z (36.7565958938682 -1.36954724767579 0,36.7565958938682 -1.36954724767579 0) | [5 empty] | -1 | 0 | -1 |  |  | 312620378 | hardy SECONDARY TAPLIN | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY TAPLIN | 193 | Langa'Ta | Hardy |  | 312620378 | 0 |  | LINESTRING Z (36.7565958938682 -1.36954724767579 0,36.7565958938682 -1.36954724767579 0) |  |  |  | TP016
LINESTRING Z (36.7666444907395 -1.36618876197399 0,36.7666444907395 -1.36618876197399 0) | [5 empty] | -1 | 0 | -1 |  |  | 312000425 | hardy SECONDARY TAPLIN | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY TAPLIN | 194 | Mugumoini | Bomas |  | 312000425 | 0 |  | LINESTRING Z (36.7666444907395 -1.36618876197399 0,36.7666444907395 -1.36618876197399 0) |  |  |  | TP012
LINESTRING Z (36.763526981731 -1.36789570407714 0,36.763526981731 -1.36789570407714 0) | [5 empty] | -1 | 0 | -1 |  |  | 312620376 | hardy SECONDARY TAPLIN | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY TAPLIN | 195 | Langa'Ta | Hardy |  | 312620376 | 0 |  | LINESTRING Z (36.763526981731 -1.36789570407714 0,36.763526981731 -1.36789570407714 0) |  |  |  | TP013
LINESTRING Z (36.7624223632652 -1.37265521504387 0,36.7624223632652 -1.37265521504387 0) | [5 empty] | -1 | 0 | -1 |  |  | 312000614 | hardy SECONDARY TAPLIN | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY TAPLIN | 196 | Langa'Ta | Hardy |  | 312000614 | 0 |  | LINESTRING Z (36.7624223632652 -1.37265521504387 0,36.7624223632652 -1.37265521504387 0) |  |  |  | TP035
LINESTRING Z (36.7616372656626 -1.35898377956509 0,36.7616372656626 -1.35898377956509 0) | [5 empty] | -1 | 0 | -1 |  |  | 312627031 | hardy SECONDARY TAPLIN | /home/adrian/Desktop/OLDNOTEBOOKS/GIS/Kenya/hardy_feeder/hardy_full_kmz/hardy.kmz¦layername=SECONDARY TAPLIN | 197 | Langa'Ta | Hardy |  | 312627031 | 0 |  | LINESTRING Z (36.7616372656626 -1.35898377956509 0,36.7616372656626 -1.35898377956509 0) |  |  |  | TP00408
LINESTRING Z (36.7612166137447 -1.38256040644122 0,36.7634808969931 -1.38318627085982 0,36.7634808969931 -1.38318627085982 0,36.7634808969931 -1.38318627085982 0,36.7634808969931 -1.38318627085982 0,36.7634808969931 -1.38318627085982 0,36.7634808969931 -1.38318627085982 0,36.7634808969931 -1.38318627085982 0,36.7634808969931 -1.38318627085982 0) | xtra | [12 empty] | 1001 |  |  |  |  | 0.262 |  | LINESTRING Z (36.7612166137447 -1.38256040644122 0,36.7634808969931 -1.38318627085982 0,36.7634808969931 -1.38318627085982 0,36.7634808969931 -1.38318627085982 0,36.7634808969931 -1.38318627085982 0,36.7634808969931 -1.38318627085982 0,36.7634808969931 -1.38318627085982 0,36.7634808969931 -1.38318627085982 0,36.7634808969931 -1.38318627085982 0)
LINESTRING Z (36.7463032038169 -1.38080988757234 0,36.7460346937503 -1.38184023337188 0) | x3 | [12 empty] | 1002 |  |  |  |  | 0.119 |  | LINESTRING Z (36.7463032038169 -1.38080988757234 0,36.7460346937503 -1.38184023337188 0)

## line_connection
from | to | no
2009 | 1670 | 32 | 2009 -1670 | 32
459 | 458 | 33 | 459 -458 | 33
32013T | node15 | 35 | 32013T -node15 | 35
446 | node20 | 36 | 446 -node20 | 36
13129 | 00453B | 40 | 13129 -00453B | 40
node1 | 463 | 42 | node1 -463 | 42
467 | 2009 | 43 | 467 -2009 | 43
node12 | 2038 | 44 | node12 -2038 | 44
466 | node18 | 45 | 466 -node18 | 45
465 | node16 | 46 | 465 -node16 | 46
node6a | 106601 | 47 | node6a -106601 | 47
449 | 446 | 48 | 449 -446 | 48
12747 | 136305 | 50 | 12747 -136305 | 50
136305 | node26 | 52 | 136305 -node26 | 52
node26 | 165257 | 53 | node26 -165257 | 53
node26 | NO.NO.1 | 55 | node26 -NO.NO.1 | 55
04058A | node4 | 56 | 04058A -node4 | 56
node10 | node11 | 59 | node10 -node11 | 59
node9 | node10 | 60 | node9 -node10 | 60
NO.NO.1 | 4001 | 62 | NO.NO.1 -4001 | 62
node17 | 449 | 64 | node17 -449 | 64
node7 | 16253 | 66 | node7 -16253 | 66
13595 | node13 | 68 | 13595 -node13 | 68
node12 | 13595 | 69 | node12 -13595 | 69
node13 | 459 | 70 | node13 -459 | 70
457 | 16041 | 71 | 457 -16041 | 71
463 | 2037 | 72 | 463 -2037 | 72
langata_tx | 12747 | 74 | langata_tx -12747 | 74
node23 | 45161 | 75 | node23 -45161 | 75
45161 | 127138 | 78 | 45161 -127138 | 78
node8 | node9 | 79 | node8 -node9 | 79
node16 | 466 | 80 | node16 -466 | 80
node15 | node1 | 81 | node15 -node1 | 81
node15 | 461 | 82 | node15 -461 | 82
node18 | 467 | 84 | node18 -467 | 84
node6b | 12105 | 85 | node6b -12105 | 85
node16 | 2189 | 86 | node16 -2189 | 86
464 | node17 | 87 | 464 -node17 | 87
3907 | 13073 | 89 | 3907 -13073 | 89
node7 | node6a | 91 | node7 -node6a | 91
node6a | 1956 | 91 | node6a -1956 | 91
node5 | node6 | 92 | node5 -node6 | 92
node11 | node24 | 93 | node11 -node24 | 93
14156 | node12 | 94 | 14156 -node12 | 94
458 | 457 | 95 | 458 -457 | 95
node13 | node14 | 96 | node13 -node14 | 96
node6 | 409 | 97 | node6 -409 | 97
node10 | 32027 | 98 | node10 -32027 | 98
409 | node7 | 99 | 409 -node7 | 99
node1 | 00462B | 100 | node1 -00462B | 100
12105 | node8 | 101 | 12105 -node8 | 101
node14 | 460 | 102 | node14 -460 | 102
node14 | 32013T | 103 | node14 -32013T | 103
node25 | 14156 | 104 | node25 -14156 | 104
node24 | node25 | 105 | node24 -node25 | 105
node23 | 456 | 106 | node23 -456 | 106
node17 | 465 | 107 | node17 -465 | 107
node20 | node2 | 108 | node20 -node2 | 108
node2 | 33950 | 110 | node2 -33950 | 110
node2 | 447 | 111 | node2 -447 | 111
node4 | node5 | 113 | node4 -node5 | 113
node20 | node21 | 114 | node20 -node21 | 114
node4 | 404 | 118 | node4 -404 | 118
4001 | node3 | 119 | 4001 -node3 | 119
node3 | 04058A | 120 | node3 -04058A | 120
433 | 13129 | 122 | 433 -13129 | 122
136305 | 13708 | 123 | 136305 -13708 | 123
04970B | node23 | 124 | 04970B -node23 | 124
13546 | 433 | 125 | 13546 -433 | 125
455 | 04970B | 127 | 455 -04970B | 127
node3 | 13546 | 128 | node3 -13546 | 128
32013T | 464 | 129 | 32013T -464 | 129
node22 | 106612 | 131 | node22 -106612 | 131
node6 | node6b | 132 | node6 -node6b | 132
node21 | 3907 | 133 | node21 -3907 | 133
node6b | 00454NR | 135 | node6b -00454NR | 135
node9 | 408 | 137 | node9 -408 | 137
node25 | 169238 | 138 | node25 -169238 | 138
00454NR | node22 | 139 | 00454NR -node22 | 139
2009 | node19 | 141 | 2009 -node19 | 141
450 | 16370 | 142 | 450 -16370 | 142
node8 | 117295 | 143 | node8 -117295 | 143
node18 | 450 | 144 | node18 -450 | 144
node11 | 455 | 145 | node11 -455 | 145
node24 | 32287 | 176 | node24 -32287 | 176
node19 | 1671 | 1001 | node19 -1671 | 1001
node21 | 168973 | 1002 | node21 -168973 | 1002
node5 | 106600 | 134112 | node5 -106600 | 134112
node22 | 175528 | 140,19 | node22 -175528 | 140,19

## bus
| name | name_II | bus_name |  | v_nom | v_mag_pu_set | in_service | v_mag_pu_min | v_mag_pu_max | x | y | x1 | y1 |  | coords
0 | 00453B 0.415 | 00453B | 00453B-K.B.C._LANGATA 0.415 | 0 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7471 | -1.3571 | 36.7471 | -1.3571 | 0 | 36.7471094242747,-1.35713395967179
1 | 00454NR 0.415 | 00454NR | 00454NR-BOGANI EAST ROAD_III 0.415 | 1 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7585 | -1.3564 | 36.7585 | -1.3564 | 1 | 36.7584725839617,-1.35639817290244
2 | 00462B 0.415 | 00462B | 00462B-K.C.C.T_MBAGATHI 0.415 | 2 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7667 | -1.3805 | 36.7667 | -1.3805 | 2 | 36.7667231620065,-1.38047793835761
3 | 04058A 0.415 | 04058A | 04058A-BOGANI EAST ROAD_0 0.415 | 3 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7569 | -1.3527 | 36.7569 | -1.3527 | 3 | 36.7569132002294,-1.35272869876763
4 | 04970B 0.415 | 04970B | 04970B-BURHANIYA SCHOOL 0.415 | 4 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7594 | -1.3639 | 36.7594 | -1.3639 | 4 | 36.7594311309821,-1.36389019607431
5 | 106600 0.415 | 106600 | 106600-106600 0.415 | 5 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7606 | -1.3529 | 36.7606 | -1.3529 | 5 | 36.7605795763563,-1.35286426923963
6 | 106601 0.415 | 106601 | 106601-NEAR BROOKHOUSE SCHOOL 0.415 | 6 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7621 | -1.3471 | 36.7621 | -1.3471 | 6 | 36.762076283107,-1.34714933688208
7 | 106612 0.415 | 106612 | 106612-106612 0.415 | 7 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7555 | -1.3569 | 36.7555 | -1.3569 | 7 | 36.7554608025107,-1.35688558713458
8 | 117295 0.415 | 117295 | 117295-BBROOD KENYA LIMITED 0.415 | 8 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7616 | -1.3567 | 36.7616 | -1.3567 | 8 | 36.7616185428589,-1.35672560455267
9 | 12105 0.415 | 12105 | 12105-PARK PLACE HOTEL 0.415 | 9 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7618 | -1.3559 | 36.7618 | -1.3559 | 9 | 36.7618156185011,-1.35592046277368
10 | 127138 0.415 | 127138 | 127138-DAWAT 2 0.415 | 10 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7546 | -1.361 | 36.7546 | -1.361 | 10 | 36.7545773444594,-1.36095430482037
11 | 12747 0.415 | 12747 | 12747-APOSTLES OF JESUS 0.415 | 11 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7577 | -1.3433 | 36.7577 | -1.3433 | 11 | 36.7577418860007,-1.34328854424595
12 | 13073 0.415 | 13073 | 13073-GATAKA WATER SUPPLY 0.415 | 12 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.749 | -1.3815 | 36.749 | -1.3815 | 12 | 36.749047924785,-1.38149034139184
13 | 13129 0.415 | 13129 | 13129-BOGANI EAST ROAD_I 0.415 | 13 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7503 | -1.3536 | 36.7503 | -1.3536 | 13 | 36.7503475000925,-1.35358701297463
14 | 13546 0.415 | 13546 | 13546-BOGANI EAST ROAD_II 0.415 | 14 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7548 | -1.3531 | 36.7548 | -1.3531 | 14 | 36.7548357734722,-1.35305642471318
15 | 13595 0.415 | 13595 | 13595-BANDA PREPARATORY SCH. 0.415 | 15 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7666 | -1.3662 | 36.7666 | -1.3662 | 15 | 36.7666444907395,-1.36618876197399
16 | 136305 0.415 | 136305 | 136305-NORKAN S.TREATMENT PLANT 0.415 | 16 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7568 | -1.3469 | 36.7568 | -1.3469 | 16 | 36.7568232402855,-1.34692593186729
17 | 13708 0.415 | 13708 | 13708-ST. AQUINAS SEMINARY 0.415 | 17 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.754 | -1.3472 | 36.754 | -1.3472 | 17 | 36.7539687234416,-1.34724283485521
18 | 14156 0.415 | 14156 | 14156-NETWORK INTERNATIONAL 0.415 | 18 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.765 | -1.3636 | 36.765 | -1.3636 | 18 | 36.7649949841971,-1.36363436841892
19 | 16041 0.415 | 16041 | 16041-BANDA ROAD_KISEMBE 0.415 | 19 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7566 | -1.3695 | 36.7566 | -1.3695 | 19 | 36.7565958938682,-1.36954724767579
20 | 16253 0.415 | 16253 | 16253-BROOKE HOUSE SCHOOL_0 0.415 | 20 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7654 | -1.346 | 36.7654 | -1.346 | 20 | 36.7654302091879,-1.34598825744552
21 | 16370 0.415 | 16370 | 16370-KIKENI DRIVE 0.415 | 21 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7567 | -1.381 | 36.7567 | -1.381 | 21 | 36.7567183085312,-1.38099466561844
22 | 165257 0.415 | 165257 | 165257-CATHOLIC UNIVERSITY_I 0.415 | 22 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7579 | -1.35 | 36.7579 | -1.35 | 22 | 36.757891416378,-1.3499707011205
23 | 1670 0.415 | 1670 | 1670-MUNDERENDU ROAD_LANGATA 0.415 | 23 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7645 | -1.3782 | 36.7645 | -1.3782 | 23 | 36.7644866512733,-1.37824857283834
24 | 1671 0.415 | 1671 | 1671-MUHUTI ROAD_LANGATA 0.415 | 24 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7635 | -1.3832 | 36.7635 | -1.3832 | 24 | 36.7634672835673,-1.38317905863203
25 | 168973 0.415 | 168973 | 168973-GATAKA BOREHOLE 0.415 | 25 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.746 | -1.3818 | 36.746 | -1.3818 | 25 | 36.7460292057179,-1.38183859493755
26 | 169238 0.415 | 169238 | 169238-CAMBRIDGE 0.415 | 26 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7646 | -1.3634 | 36.7646 | -1.3634 | 26 | 36.7645527914373,-1.36342505805443
27 | 175528 0.415 | 175528 | 175528-CATHOLIC UNIVERSITY OF E A 0.415 | 27 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7555 | -1.3571 | 36.7555 | -1.3571 | 27 | 36.7554793265145,-1.3571046954011
28 | 1956 0.415 | 1956 | 1956-BROOKE HOUSE SCHOOL_I 0.415 | 28 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7633 | -1.3466 | 36.7633 | -1.3466 | 28 | 36.7633226633752,-1.34656625225938
29 | 2009 0.415 | 2009 | 2009-MUNDERENDU RD_LANGATA 0.415 | 29 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7612 | -1.3796 | 36.7612 | -1.3796 | 29 | 36.7612068626399,-1.37964570579744
30 | 2037 0.415 | 2037 | 2037-KENYA NATIONAL PARK_0 0.415 | 30 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7749 | -1.3786 | 36.7749 | -1.3786 | 30 | 36.7748666444081,-1.37859409878224
31 | 2038 0.415 | 2038 | 2038-KENYA NATIONAL PARK 0.415 | 31 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7673 | -1.3638 | 36.7673 | -1.3638 | 31 | 36.7673305364644,-1.36377539781515
32 | 2189 0.415 | 2189 | 2189-NDOROBO ROAD_0 0.415 | 32 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7603 | -1.3755 | 36.7603 | -1.3755 | 32 | 36.7602629004934,-1.37549780111096
33 | 32013T 0.415 | 32013T | 32013T-KISEMBE PUMP_0 0.415 | 33 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7682 | -1.372 | 36.7682 | -1.372 | 33 | 36.7681820421319,-1.37197221229169
34 | 32027 0.415 | 32027 | 32027-DEWAT E. HADIYA_I 0.415 | 34 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.761 | -1.3608 | 36.761 | -1.3608 | 34 | 36.7609651864401,-1.36078082293381
35 | 32287 0.415 | 32287 | 32287-SAIFEE PARK_MAGADI RD_0 0.415 | 35 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7638 | -1.3621 | 36.7638 | -1.3621 | 35 | 36.7637952838629,-1.36213885472542
36 | 33950 0.415 | 33950 | 33950-SIMBA HILL ROAD_0 0.415 | 36 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7411 | -1.3742 | 36.7411 | -1.3742 | 36 | 36.7410896562047,-1.37418876869938
37 | 3907 0.415 | 3907 | 3907-PARK VIEW EST._LANGATA 0.415 | 37 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7472 | -1.381 | 36.7472 | -1.381 | 37 | 36.7471553579504,-1.38099637926356
38 | 4001 0.415 | 4001 | 4001-CATHOLIC UNIVERSITY_0 0.415 | 38 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7563 | -1.3517 | 36.7563 | -1.3517 | 38 | 36.756256521237,-1.35172476577396
39 | 404 0.415 | 404 | 404-ST.THOMAS SEMINARY 0.415 | 39 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7586 | -1.3487 | 36.7586 | -1.3487 | 39 | 36.7586495558373,-1.34867344535816
40 | 408 0.415 | 408 | 408-MAGADI ROAD 0.415 | 40 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7616 | -1.359 | 36.7616 | -1.359 | 40 | 36.7616372656626,-1.35898377956509
41 | 409 0.415 | 409 | 409-BOGANI ROAD_V 0.415 | 41 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.763 | -1.3505 | 36.763 | -1.3505 | 41 | 36.763036432869,-1.35049720568309
42 | 433 0.415 | 433 | 433-BOGANI EAST ROAD_IV 0.415 | 42 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7531 | -1.3533 | 36.7531 | -1.3533 | 42 | 36.7531188035318,-1.35326474608744
43 | 446 0.415 | 446 | 446-PARK VIEW_LANGATA 0.415 | 43 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7466 | -1.3745 | 36.7466 | -1.3745 | 43 | 36.7465582726068,-1.37450408676786
44 | 447 0.415 | 447 | 447-SIMBA HILL ROAD_I 0.415 | 44 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7412 | -1.3773 | 36.7412 | -1.3773 | 44 | 36.7412361387439,-1.37728738234144
45 | 449 0.415 | 449 | 449-KISEMBE EAST 0.415 | 45 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7505 | -1.3741 | 36.7505 | -1.3741 | 45 | 36.7505226572627,-1.37408454262385
46 | 450 0.415 | 450 | 450-KIKENI ROAD 0.415 | 46 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7568 | -1.3791 | 36.7568 | -1.3791 | 46 | 36.7567865754473,-1.37905058253932
47 | 45161 0.415 | 45161 | 45161-DAWAT E HADIYA_0 0.415 | 47 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7566 | -1.3614 | 36.7566 | -1.3614 | 47 | 36.7565940277503,-1.36136318895282
48 | 455 0.415 | 455 | 455-SAIFEE PARK_MAGADI RD_I 0.415 | 48 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7618 | -1.3618 | 36.7618 | -1.3618 | 48 | 36.7618227067845,-1.36177241961839
49 | 456 0.415 | 456 | 456-KIPEVU ROAD 0.415 | 49 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7552 | -1.3632 | 36.7552 | -1.3632 | 49 | 36.7552123181797,-1.3632251871156
50 | 457 0.415 | 457 | 457-BANDA ROAD_KISEMBE_II 0.415 | 50 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7576 | -1.3683 | 36.7576 | -1.3683 | 50 | 36.7575736263158,-1.36825584429273
51 | 458 0.415 | 458 | 458-KISEMBE ROAD 0.415 | 51 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7608 | -1.3681 | 36.7608 | -1.3681 | 51 | 36.7608369568325,-1.36805173513509
52 | 459 0.415 | 459 | 459-KISEMBE ESTATE_0 0.415 | 52 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7635 | -1.3679 | 36.7635 | -1.3679 | 52 | 36.763526981731,-1.36789570407714
53 | 460 0.415 | 460 | 460-KISEMBE PUMP_I 0.415 | 53 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7662 | -1.37 | 36.7662 | -1.37 | 53 | 36.7661985846384,-1.37000010459701
54 | 461 0.415 | 461 | 461-MMU 0.415 | 54 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7682 | -1.3763 | 36.7682 | -1.3763 | 54 | 36.768206929511,-1.37629011528426
55 | 463 0.415 | 463 | 463-K.W.S_B/HOLE 0.415 | 55 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7733 | -1.3796 | 36.7733 | -1.3796 | 55 | 36.7732945605242,-1.37963397207946
56 | 464 0.415 | 464 | 464-KISEMBE ESTATE_I 0.415 | 56 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7624 | -1.3727 | 36.7624 | -1.3727 | 56 | 36.7624223632652,-1.37265521504387
57 | 465 0.415 | 465 | 465-NDOROBO ROAD_I 0.415 | 57 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7579 | -1.3735 | 36.7579 | -1.3735 | 57 | 36.7579264893446,-1.37349144029173
58 | 466 0.415 | 466 | 466-NDOROBO ROAD_III 0.415 | 58 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7582 | -1.3758 | 36.7582 | -1.3758 | 58 | 36.7582431679171,-1.37584084408693
59 | 467 0.415 | 467 | 467-NDOROBO ROAD_II 0.415 | 59 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7587 | -1.38 | 36.7587 | -1.38 | 59 | 36.7586892630442,-1.38004691996939
60 | NO.NO.1 0.415 | NO.NO.1 | NO.NO.1-CATHOLIC UNIVERSITY 0.415 | 60 | 0.415 | 1 | 1 | 0.95 | 1.05 | 36.7563 | -1.3508 | 36.7563 | -1.3508 | 60 | 36.7563236410844,-1.35075336316955
61 | 106600 | 106600 | 106600 | 61 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7606 | -1.3529 | 36.7606 | -1.3529 | 61 | 36.7605795763563,-1.35286426923963
62 | 106612 | 106612 | 106612 | 62 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7555 | -1.3569 | 36.7749 | -1.3786 | 62 | 36.7748666444081,-1.37859409878224
63 | 12747 | 12747 | APOSTLES OF JESUS | 63 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7577 | -1.3433 | 36.7577 | -1.3433 | 63 | 36.7577418860007,-1.34328854424595
64 | 13595 | 13595 | BANDA PREPARATORY SCH. | 64 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7666 | -1.3662 | 36.7666 | -1.3662 | 64 | 36.7666444907395,-1.36618876197399
65 | 16041 | 16041 | BANDA ROAD_KISEMBE | 65 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7566 | -1.3695 | 36.7566 | -1.3695 | 65 | 36.7565958938682,-1.36954724767579
66 | 457 | 457 | BANDA ROAD_KISEMBE_II | 66 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7576 | -1.3683 | 36.7576 | -1.3683 | 66 | 36.7575736263158,-1.36825584429273
67 | 117295 | 117295 | BBROOD KENYA LIMITED | 67 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7616 | -1.3567 | 36.7616 | -1.3567 | 67 | 36.7616185428589,-1.35672560455267
68 | 04058A | 04058A | BOGANI EAST ROAD_0 | 68 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7569 | -1.3527 | 36.7569 | -1.3527 | 68 | 36.7569132002294,-1.35272869876763
69 | 13129 | 13129 | BOGANI EAST ROAD_I | 69 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7503 | -1.3536 | 36.7503 | -1.3536 | 69 | 36.7503475000925,-1.35358701297463
70 | 13546 | 13546 | BOGANI EAST ROAD_II | 70 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7548 | -1.3531 | 36.7548 | -1.3531 | 70 | 36.7548357734722,-1.35305642471318
71 | 00454NR | 00454NR | BOGANI EAST ROAD_III | 71 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7585 | -1.3564 | 36.7585 | -1.3564 | 71 | 36.7584725839617,-1.35639817290244
72 | 433 | 433 | BOGANI EAST ROAD_IV | 72 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7531 | -1.3533 | 36.7531 | -1.3533 | 72 | 36.7531188035318,-1.35326474608744
73 | 409 | 409 | BOGANI ROAD_V | 73 | 11 | 1 | 1 | 0.95 | 1.05 | 36.763 | -1.3505 | 36.763 | -1.3505 | 73 | 36.763036432869,-1.35049720568309
74 | 16253 | 16253 | BROOKE HOUSE SCHOOL_0 | 74 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7654 | -1.346 | 36.7654 | -1.346 | 74 | 36.7654302091879,-1.34598825744552
75 | 1956 | 1956 | BROOKE HOUSE SCHOOL_I | 75 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7633 | -1.3466 | 36.7633 | -1.3466 | 75 | 36.7633226633752,-1.34656625225938
76 | 04970B | 04970B | BURHANIYA SCHOOL | 76 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7594 | -1.3639 | 36.7594 | -1.3639 | 76 | 36.7594311309821,-1.36389019607431
77 | 169238 | 169238 | CAMBRIDGE | 77 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7646 | -1.3634 | 36.7646 | -1.3634 | 77 | 36.7645527914373,-1.36342505805443
78 | 4001 | 4001 | CATHOLIC UNIVERSITY_0 | 78 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7563 | -1.3517 | 36.7563 | -1.3517 | 78 | 36.756256521237,-1.35172476577396
79 | 175528 | 175528 | CATHOLIC UNIVERSITY OF E A | 79 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7555 | -1.3571 | 36.7555 | -1.3571 | 79 | 36.7554793265145,-1.3571046954011
80 | 165257 | 165257 | CATHOLIC UNIVERSITY_I | 80 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7579 | -1.35 | 36.7579 | -1.35 | 80 | 36.757891416378,-1.3499707011205
81 | NO.NO.1 | NO.NO.1 | CATHOLIC UNIVERSITY_II | 81 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7563 | -1.3508 | 36.7563 | -1.3508 | 81 | 36.7563236410844,-1.35075336316955
82 | 127138 | 127138 | DAWAT 2 | 82 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7546 | -1.361 | 36.7546 | -1.361 | 82 | 36.7545773444594,-1.36095430482037
83 | 45161 | 45161 | DAWAT E HADIYA_0 | 83 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7566 | -1.3614 | 36.7566 | -1.3614 | 83 | 36.7565940277503,-1.36136318895282
84 | 32027 | 32027 | DEWAT E. HADIYA_I | 84 | 11 | 1 | 1 | 0.95 | 1.05 | 36.761 | -1.3608 | 36.761 | -1.3608 | 84 | 36.7609651864401,-1.36078082293381
85 | 168973 | 168973 | GATAKA BOREHOLE | 85 | 11 | 1 | 1 | 0.95 | 1.05 | 36.746 | -1.3818 | 36.746 | -1.3818 | 85 | 36.7460292057179,-1.38183859493755
86 | 13073 | 13073 | GATAKA WATER SUPPLY | 86 | 11 | 1 | 1 | 0.95 | 1.05 | 36.749 | -1.3815 | 36.749 | -1.3815 | 86 | 36.749047924785,-1.38149034139184
87 | 00453B | 00453B | K.B.C._LANGATA | 87 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7471 | -1.3571 | 36.7471 | -1.3571 | 87 | 36.7471094242747,-1.35713395967179
88 | 00462B | 00462B | K.C.C.T_MBAGATHI | 88 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7667 | -1.3805 | 36.7667 | -1.3805 | 88 | 36.7667231620065,-1.38047793835761
89 | 463 | 463 | K.W.S_B/HOLE | 89 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7733 | -1.3796 | 36.7733 | -1.3796 | 89 | 36.7732945605242,-1.37963397207946
90 | 2038 | 2038 | KENYA NATIONAL PARK | 90 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7673 | -1.3638 | 36.7673 | -1.3638 | 90 | 36.7673305364644,-1.36377539781515
91 | 2037 | 2037 | KENYA NATIONAL PARK_0 | 91 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7749 | -1.3786 | 36.7749 | -1.3786 | 91 | 36.7748666444081,-1.37859409878224
92 | 16370 | 16370 | KIKENI DRIVE | 92 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7567 | -1.381 | 36.7567 | -1.381 | 92 | 36.7567183085312,-1.38099466561844
93 | 450 | 450 | KIKENI ROAD | 93 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7568 | -1.3791 | 36.7568 | -1.3791 | 93 | 36.7567865754473,-1.37905058253932
94 | 456 | 456 | KIPEVU ROAD | 94 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7552 | -1.3632 | 36.7552 | -1.3632 | 94 | 36.7552123181797,-1.3632251871156
95 | 449 | 449 | KISEMBE EAST | 95 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7505 | -1.3741 | 36.7505 | -1.3741 | 95 | 36.7505226572627,-1.37408454262385
96 | 459 | 459 | KISEMBE ESTATE_0 | 96 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7635 | -1.3679 | 36.7635 | -1.3679 | 96 | 36.763526981731,-1.36789570407714
97 | 464 | 464 | KISEMBE ESTATE_I | 97 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7624 | -1.3727 | 36.7624 | -1.3727 | 97 | 36.7624223632652,-1.37265521504387
98 | 32013T | 32013T | KISEMBE PUMP_0 | 98 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7682 | -1.372 | 36.7682 | -1.372 | 98 | 36.7681820421319,-1.37197221229169
99 | 460 | 460 | KISEMBE PUMP_I | 99 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7662 | -1.37 | 36.7662 | -1.37 | 99 | 36.7661985846384,-1.37000010459701
100 | 458 | 458 | KISEMBE ROAD | 100 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7608 | -1.3681 | 36.7608 | -1.3681 | 100 | 36.7608369568325,-1.36805173513509
101 | langata_tx | langata_tx | langata_tx | 101 | 11 | 1 | 1 | 0.95 | 1.05 | 36.758 | -1.3421 | 36.758 | -1.3421 | 101 | 36.7579665525604,-1.34209999724138
102 | 408 | 408 | MAGADI ROAD | 102 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7616 | -1.359 | 36.7616 | -1.359 | 102 | 36.7616372656626,-1.35898377956509
103 | 461 | 461 | MMU | 103 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7682 | -1.3763 | 36.7682 | -1.3763 | 103 | 36.768206929511,-1.37629011528426
104 | 1671 | 1671 | MUHUTI ROAD_LANGATA | 104 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7635 | -1.3832 | 36.7635 | -1.3832 | 104 | 36.7634672835673,-1.38317905863203
105 | 2009 | 2009 | MUNDERENDU RD_LANGATA | 105 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7612 | -1.3796 | 36.7612 | -1.3796 | 105 | 36.7612068626399,-1.37964570579744
106 | 1670 | 1670 | MUNDERENDU ROAD_LANGATA | 106 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7645 | -1.3782 | 36.7645 | -1.3782 | 106 | 36.7644866512733,-1.37824857283834
107 | 2189 | 2189 | NDOROBO ROAD_0 | 107 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7603 | -1.3755 | 36.7603 | -1.3755 | 107 | 36.7602629004934,-1.37549780111096
108 | 465 | 465 | NDOROBO ROAD_I | 108 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7579 | -1.3735 | 36.7579 | -1.3735 | 108 | 36.7579264893446,-1.37349144029173
109 | 467 | 467 | NDOROBO ROAD_II | 109 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7587 | -1.38 | 36.7587 | -1.38 | 109 | 36.7586892630442,-1.38004691996939
110 | 466 | 466 | NDOROBO ROAD_III | 110 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7582 | -1.3758 | 36.7582 | -1.3758 | 110 | 36.7582431679171,-1.37584084408693
111 | 106601 | 106601 | NEAR BROOKHOUSE SCHOOL | 111 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7621 | -1.3471 | 36.7621 | -1.3471 | 111 | 36.762076283107,-1.34714933688208
112 | 14156 | 14156 | NETWORK INTERNATIONAL | 112 | 11 | 1 | 1 | 0.95 | 1.05 | 36.765 | -1.3636 | 36.765 | -1.3636 | 112 | 36.7649949841971,-1.36363436841892
113 | node1 | node1 | node1 | 113 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7699 | -1.38 | 36.7699 | -1.38 | 113 | 36.7698813824731,-1.38001194403103
114 | node10 | node10 | node10 | 114 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7623 | -1.3607 | 36.7623 | -1.3607 | 114 | 36.7622855261742,-1.36069603276204
115 | node11 | node11 | node11 | 115 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7625 | -1.3609 | 36.7625 | -1.3609 | 115 | 36.7624931584252,-1.3609281124923
116 | node12 | node12 | node12 | 116 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7659 | -1.3649 | 36.7659 | -1.3649 | 116 | 36.76591701561,-1.36494782278443
117 | node13 | node13 | node13 | 117 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7674 | -1.3682 | 36.7674 | -1.3682 | 117 | 36.7673984075653,-1.36823663832402
118 | node14 | node14 | node14 | 118 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7671 | -1.37 | 36.7671 | -1.37 | 118 | 36.7670765841199,-1.36999879607117
119 | node15 | node15 | node15 | 119 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7692 | -1.3759 | 36.7692 | -1.3759 | 119 | 36.7692169954759,-1.37588183070028
120 | node16 | node16 | node16 | 120 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7582 | -1.3754 | 36.7582 | -1.3754 | 120 | 36.7581961720968,-1.37541704664815
121 | node17 | node17 | node17 | 121 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7579 | -1.3732 | 36.7579 | -1.3732 | 121 | 36.757888759798,-1.37319733022595
122 | node18 | node18 | node18 | 122 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7586 | -1.3789 | 36.7586 | -1.3789 | 122 | 36.7585500007543,-1.3788663993872
123 | node19 | node19 | node19 | 123 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7612 | -1.3826 | 36.7612 | -1.3826 | 123 | 36.7612166137447,-1.38256040644122
124 | node2 | node2 | node2 | 124 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7411 | -1.3752 | 36.7411 | -1.3752 | 124 | 36.7411357236897,-1.3751567511646
125 | node20 | node20 | node20 | 125 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7463 | -1.3745 | 36.7463 | -1.3745 | 125 | 36.7462733180924,-1.37453872997444
126 | node21 | node21 | node21 | 126 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7463 | -1.3808 | 36.7463 | -1.3808 | 126 | 36.7463050284598,-1.38080303707381
127 | node22 | node22 | node22 | 127 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7555 | -1.357 | 36.7555 | -1.357 | 127 | 36.7555190442461,-1.35702584112019
128 | node23 | node23 | node23 | 128 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7558 | -1.3631 | 36.7558 | -1.3631 | 128 | 36.7558333036587,-1.36313160563965
129 | node24 | node24 | node24 | 129 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7637 | -1.3622 | 36.7637 | -1.3622 | 129 | 36.7636846570309,-1.36223224500122
130 | node25 | node25 | node25 | 130 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7647 | -1.3633 | 36.7647 | -1.3633 | 130 | 36.7646794846246,-1.36330388643667
131 | node26 | node26 | node26 | 131 | 11 | 1 | 1 | 0.95 | 1.05 | 36.757 | -1.3493 | 36.757 | -1.3493 | 131 | 36.7570291160282,-1.34932128908751
132 | node3 | node3 | node3 | 132 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7564 | -1.3528 | 36.7564 | -1.3528 | 132 | 36.7563878830746,-1.35283104378804
133 | node4 | node4 | node4 | 133 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7589 | -1.3525 | 36.7589 | -1.3525 | 133 | 36.7589102901439,-1.35254987804557
134 | node5 | node5 | node5 | 134 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7603 | -1.3524 | 36.7603 | -1.3524 | 134 | 36.7603337106913,-1.35236395032121
135 | node6 | node6 | node6 | 135 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7624 | -1.3519 | 36.7624 | -1.3519 | 135 | 36.7623921963995,-1.35194549133002
136 | node6a | node6a | node6a | 136 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7634 | -1.3467 | 36.7634 | -1.3467 | 136 | 36.7633764169857,-1.34667459800873
137 | node6b | node6b | node6b | 137 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7618 | -1.3558 | 36.7618 | -1.3558 | 137 | 36.7617961576617,-1.35583823096373
138 | node7 | node7 | node7 | 138 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7652 | -1.3466 | 36.7652 | -1.3466 | 138 | 36.7651574651075,-1.34656776213099
139 | node8 | node8 | node8 | 139 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7621 | -1.3567 | 36.7621 | -1.3567 | 139 | 36.7620971077276,-1.35668690737419
140 | node9 | node9 | node9 | 140 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7624 | -1.3589 | 36.7624 | -1.3589 | 140 | 36.7624322359531,-1.35891324510337
141 | 136305 | 136305 | NORKAN S.TREATMENT PLANT | 141 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7568 | -1.3469 | 36.7568 | -1.3469 | 141 | 36.7568232402855,-1.34692593186729
142 | 12105 | 12105 | PARK PLACE HOTEL | 142 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7618 | -1.3559 | 36.7618 | -1.3559 | 142 | 36.7618156185011,-1.35592046277368
143 | 3907 | 3907 | PARK VIEW EST._LANGATA | 143 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7472 | -1.381 | 36.7472 | -1.381 | 143 | 36.7471553579504,-1.38099637926356
144 | 446 | 446 | PARK VIEW_LANGATA | 144 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7466 | -1.3745 | 36.7466 | -1.3745 | 144 | 36.7465582726068,-1.37450408676786
145 | 32287 | 32287 | SAIFEE PARK_MAGADI RD_0 | 145 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7638 | -1.3621 | 36.7638 | -1.3621 | 145 | 36.7637952838629,-1.36213885472542
146 | 455 | 455 | SAIFEE PARK_MAGADI RD_I | 146 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7618 | -1.3618 | 36.7618 | -1.3618 | 146 | 36.7618227067845,-1.36177241961839
147 | 33950 | 33950 | SIMBA HILL ROAD_0 | 147 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7411 | -1.3742 | 36.7411 | -1.3742 | 147 | 36.7410896562047,-1.37418876869938
148 | 447 | 447 | SIMBA HILL ROAD_I | 148 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7412 | -1.3773 | 36.7412 | -1.3773 | 148 | 36.7412361387439,-1.37728738234144
149 | 13708 | 13708 | ST. AQUINAS SEMINARY | 149 | 11 | 1 | 1 | 0.95 | 1.05 | 36.754 | -1.3472 | 36.754 | -1.3472 | 149 | 36.7539687234416,-1.34724283485521
150 | 404 | 404 | ST.THOMAS SEMINARY | 150 | 11 | 1 | 1 | 0.95 | 1.05 | 36.7586 | -1.3487 | 36.7586 | -1.3487 | 150 | 36.7586495558373,-1.34867344535816

## lines
| name | no | from | to | type | length | from_bus | to_bus | temp | r | x | b | r0 | x0 | y0 | r1 | x1 | y1 | max_i | parallel | geodata | geometry
0 | 2009 -1670 | 32 | 2009 | 1670 |  | 0.397 | 105 | 106 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7612068626399 -1.37964570579744, 36.7644866512733 -1.37824857283834) | LINESTRING Z (36.7612068626399 -1.37964570579744 0,36.7644866512733 -1.37824857283834 0)
1 | 459 -458 | 33 | 459 | 458 |  | 0.3 | 96 | 100 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.763526981731 -1.36789570407714, 36.7608369568325 -1.36805173513509) | LINESTRING Z (36.763526981731 -1.36789570407714 0,36.7608369568325 -1.36805173513509 0)
2 | 32013T -node15 | 35 | 32013T | node15 |  | 0.45 | 98 | 119 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7692169954759 -1.37588183070028, 36.7681820421319 -1.37197221229169) | LINESTRING Z (36.7692169954759 -1.37588183070028 0,36.7681820421319 -1.37197221229169 0)
3 | 446 -node20 | 36 | 446 | node20 |  | 0.032 | 144 | 125 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7462733180924 -1.37453872997444, 36.7465582726068 -1.37450408676786) | LINESTRING Z (36.7462733180924 -1.37453872997444 0,36.7465582726068 -1.37450408676786 0)
4 | 13129 -00453B | 40 | 13129 | 00453B |  | 0.535 | 69 | 87 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7503475000925 -1.35358701297463, 36.7471094242747 -1.35713395967179) | LINESTRING Z (36.7503475000925 -1.35358701297463 0,36.7471094242747 -1.35713395967179 0)
5 | node1 -463 | 42 | node1 | 463 |  | 0.382 | 113 | 89 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7698813824731 -1.38001194403103, 36.7732945605242 -1.37963397207946) | LINESTRING Z (36.7698813824731 -1.38001194403103 0,36.7732945605242 -1.37963397207946 0)
6 | 467 -2009 | 43 | 467 | 2009 |  | 0.284 | 109 | 105 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7586892630442 -1.38004691996939, 36.7612068626399 -1.37964570579744) | LINESTRING Z (36.7586892630442 -1.38004691996939 0,36.7612068626399 -1.37964570579744 0)
7 | node12 -2038 | 44 | node12 | 2038 |  | 0.204 | 116 | 90 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.76591701561 -1.36494782278443, 36.7673305364644 -1.36377539781515) | LINESTRING Z (36.76591701561 -1.36494782278443 0,36.7673305364644 -1.36377539781515 0)
8 | 466 -node18 | 45 | 466 | node18 |  | 0.339 | 110 | 122 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7582431679171 -1.37584084408693, 36.7585500007543 -1.3788663993872) | LINESTRING Z (36.7582431679171 -1.37584084408693 0,36.7585500007543 -1.3788663993872 0)
9 | 465 -node16 | 46 | 465 | node16 |  | 0.216 | 108 | 120 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7579264893446 -1.37349144029173, 36.7581961720968 -1.37541704664815) | LINESTRING Z (36.7579264893446 -1.37349144029173 0,36.7581961720968 -1.37541704664815 0)
10 | node6a -106601 | 47 | node6a | 106601 |  | 0.154 | 136 | 111 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.762076283107 -1.34714933688208, 36.7633764169857 -1.34667459800873) | LINESTRING Z (36.762076283107 -1.34714933688208 0,36.7633764169857 -1.34667459800873 0)
11 | 449 -446 | 48 | 449 | 446 |  | 0.444 | 95 | 144 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7465582726068 -1.37450408676786, 36.7505226572627 -1.37408454262385) | LINESTRING Z (36.7465582726068 -1.37450408676786 0,36.7505226572627 -1.37408454262385 0)
12 | 12747 -136305 | 50 | 12747 | 136305 |  | 0.418 | 63 | 141 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7568232402855 -1.34692593186729, 36.7577418860007 -1.34328854424595) | LINESTRING Z (36.7568232402855 -1.34692593186729 0,36.7577418860007 -1.34328854424595 0)
13 | 136305 -node26 | 52 | 136305 | node26 |  | 0.268 | 141 | 131 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7568232402855 -1.34692593186729, 36.7570291160282 -1.34932128908751) | LINESTRING Z (36.7568232402855 -1.34692593186729 0,36.7570291160282 -1.34932128908751 0)
14 | node26 -165257 | 53 | node26 | 165257 |  | 0.12 | 131 | 80 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7570291160282 -1.34932128908751, 36.757891416378 -1.3499707011205) | LINESTRING Z (36.7570291160282 -1.34932128908751 0,36.757891416378 -1.3499707011205 0)
15 | node26 -NO.NO.1 | 55 | node26 | NO.NO.1 |  | 0.178 | 131 | 81 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7570291160282 -1.34932128908751, 36.7563236410844 -1.35075336316955) | LINESTRING Z (36.7570291160282 -1.34932128908751 0,36.7563236410844 -1.35075336316955 0)
16 | 04058A -node4 | 56 | 04058A | node4 |  | 0.223 | 68 | 133 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7589102901439 -1.35254987804557, 36.7569132002294 -1.35272869876763) | LINESTRING Z (36.7589102901439 -1.35254987804557 0,36.7569132002294 -1.35272869876763 0)
17 | node10 -node11 | 59 | node10 | node11 |  | 0.035 | 114 | 115 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7624931584252 -1.3609281124923, 36.7622855261742 -1.36069603276204) | LINESTRING Z (36.7624931584252 -1.3609281124923 0,36.7622855261742 -1.36069603276204 0)
18 | node9 -node10 | 60 | node9 | node10 |  | 0.199 | 140 | 114 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7622855261742 -1.36069603276204, 36.7624322359531 -1.35891324510337) | LINESTRING Z (36.7622855261742 -1.36069603276204 0,36.7624322359531 -1.35891324510337 0)
19 | NO.NO.1 -4001 | 62 | NO.NO.1 | 4001 |  | 0.108 | 81 | 78 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7563236410844 -1.35075336316955, 36.756256521237 -1.35172476577396) | LINESTRING Z (36.7563236410844 -1.35075336316955 0,36.756256521237 -1.35172476577396 0)
20 | node17 -449 | 64 | node17 | 449 |  | 0.826 | 121 | 95 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7505226572627 -1.37408454262385, 36.757888759798 -1.37319733022595) | LINESTRING Z (36.7505226572627 -1.37408454262385 0,36.757888759798 -1.37319733022595 0)
21 | node7 -16253 | 66 | node7 | 16253 |  | 0.071 | 138 | 74 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7651574651075 -1.34656776213099, 36.7654302091879 -1.34598825744552) | LINESTRING Z (36.7651574651075 -1.34656776213099 0,36.7654302091879 -1.34598825744552 0)
22 | 13595 -node13 | 68 | 13595 | node13 |  | 0.243 | 64 | 117 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7673984075653 -1.36823663832402, 36.7666444907395 -1.36618876197399) | LINESTRING Z (36.7673984075653 -1.36823663832402 0,36.7666444907395 -1.36618876197399 0)
23 | node12 -13595 | 69 | node12 | 13595 |  | 0.16 | 116 | 64 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7666444907395 -1.36618876197399, 36.76591701561 -1.36494782278443) | LINESTRING Z (36.7666444907395 -1.36618876197399 0,36.76591701561 -1.36494782278443 0)
24 | node13 -459 | 70 | node13 | 459 |  | 0.433 | 117 | 96 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7673984075653 -1.36823663832402, 36.763526981731 -1.36789570407714) | LINESTRING Z (36.7673984075653 -1.36823663832402 0,36.763526981731 -1.36789570407714 0)
25 | 457 -16041 | 71 | 457 | 16041 |  | 0.18 | 66 | 65 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7575736263158 -1.36825584429273, 36.7565958938682 -1.36954724767579) | LINESTRING Z (36.7575736263158 -1.36825584429273 0,36.7565958938682 -1.36954724767579 0)
26 | 463 -2037 | 72 | 463 | 2037 |  | 0.21 | 89 | 91 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7732945605242 -1.37963397207946, 36.7748666444081 -1.37859409878224) | LINESTRING Z (36.7732945605242 -1.37963397207946 0,36.7748666444081 -1.37859409878224 0)
27 | langata_tx -12747 | 74 | langata_tx | 12747 |  | 0.135 | 101 | 63 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7579665525604 -1.34209999724138, 36.7577418860007 -1.34328854424595) | LINESTRING Z (36.7579665525604 -1.34209999724138 0,36.7577418860007 -1.34328854424595 0)
28 | node23 -45161 | 75 | node23 | 45161 |  | 0.214 | 128 | 83 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7558333036587 -1.36313160563965, 36.7565940277503 -1.36136318895282) | LINESTRING Z (36.7558333036587 -1.36313160563965 0,36.7565940277503 -1.36136318895282 0)
29 | 45161 -127138 | 78 | 45161 | 127138 |  | 0.229 | 83 | 82 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7545773444594 -1.36095430482037, 36.7565940277503 -1.36136318895282) | LINESTRING Z (36.7545773444594 -1.36095430482037 0,36.7565940277503 -1.36136318895282 0)
30 | node8 -node9 | 79 | node8 | node9 |  | 0.251 | 139 | 140 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7624322359531 -1.35891324510337, 36.7620971077276 -1.35668690737419) | LINESTRING Z (36.7624322359531 -1.35891324510337 0,36.7620971077276 -1.35668690737419 0)
31 | node16 -466 | 80 | node16 | 466 |  | 0.047 | 120 | 110 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7581961720968 -1.37541704664815, 36.7582431679171 -1.37584084408693) | LINESTRING Z (36.7581961720968 -1.37541704664815 0,36.7582431679171 -1.37584084408693 0)
32 | node15 -node1 | 81 | node15 | node1 |  | 0.466 | 119 | 113 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7692169954759 -1.37588183070028, 36.7698813824731 -1.38001194403103) | LINESTRING Z (36.7692169954759 -1.37588183070028 0,36.7698813824731 -1.38001194403103 0)
33 | node15 -461 | 82 | node15 | 461 |  | 0.121 | 119 | 103 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.768206929511 -1.37629011528426, 36.7692169954759 -1.37588183070028) | LINESTRING Z (36.768206929511 -1.37629011528426 0,36.7692169954759 -1.37588183070028 0)
34 | node18 -467 | 84 | node18 | 467 |  | 0.132 | 122 | 109 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7585500007543 -1.3788663993872, 36.7586892630442 -1.38004691996939) | LINESTRING Z (36.7585500007543 -1.3788663993872 0,36.7586892630442 -1.38004691996939 0)
35 | node6b -12105 | 85 | node6b | 12105 |  | 0.009 | 137 | 142 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7618156185011 -1.35592046277368, 36.7617961576617 -1.35583823096373) | LINESTRING Z (36.7618156185011 -1.35592046277368 0,36.7617961576617 -1.35583823096373 0)
36 | node16 -2189 | 86 | node16 | 2189 |  | 0.23 | 120 | 107 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7581961720968 -1.37541704664815, 36.7602629004934 -1.37549780111096) | LINESTRING Z (36.7581961720968 -1.37541704664815 0,36.7602629004934 -1.37549780111096 0)
37 | 464 -node17 | 87 | 464 | node17 |  | 0.508 | 97 | 121 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7624223632652 -1.37265521504387, 36.757888759798 -1.37319733022595) | LINESTRING Z (36.7624223632652 -1.37265521504387 0,36.757888759798 -1.37319733022595 0)
38 | 3907 -13073 | 89 | 3907 | 13073 |  | 0.218 | 143 | 86 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7471553579504 -1.38099637926356, 36.749047924785 -1.38149034139184) | LINESTRING Z (36.7471553579504 -1.38099637926356 0,36.749047924785 -1.38149034139184 0)
39 | node7 -node6a | 91 | node7 | node6a |  | 0.212 | 138 | 136 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7651574651075 -1.34656776213099, 36.7633764169857 -1.34667459800873,36.7633226633752 | LINESTRING Z (36.7651574651075 -1.34656776213099 0,36.7633764169857 -1.34667459800873 0,36.7633226633752 -1.34656625225938 0)
40 | node6a -1956 | 91 | node6a | 1956 |  | 0.212 | 136 | 75 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7651574651075 -1.34656776213099, 36.7633764169857 -1.34667459800873,36.7633226633752 | LINESTRING Z (36.7651574651075 -1.34656776213099 0,36.7633764169857 -1.34667459800873 0,36.7633226633752 -1.34656625225938 0)
41 | node5 -node6 | 92 | node5 | node6 |  | 0.234 | 134 | 135 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7623921963995 -1.35194549133002, 36.7603337106913 -1.35236395032121) | LINESTRING Z (36.7623921963995 -1.35194549133002 0,36.7603337106913 -1.35236395032121 0)
42 | node11 -node24 | 93 | node11 | node24 |  | 0.197 | 115 | 129 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7636846570309 -1.36223224500122, 36.7624931584252 -1.3609281124923) | LINESTRING Z (36.7636846570309 -1.36223224500122 0,36.7624931584252 -1.3609281124923 0)
43 | 14156 -node12 | 94 | 14156 | node12 |  | 0.179 | 112 | 116 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.76591701561 -1.36494782278443, 36.7649949841971 -1.36363436841892) | LINESTRING Z (36.76591701561 -1.36494782278443 0,36.7649949841971 -1.36363436841892 0)
44 | 458 -457 | 95 | 458 | 457 |  | 0.364 | 100 | 66 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7608369568325 -1.36805173513509, 36.7575736263158 -1.36825584429273) | LINESTRING Z (36.7608369568325 -1.36805173513509 0,36.7575736263158 -1.36825584429273 0)
45 | node13 -node14 | 96 | node13 | node14 |  | 0.199 | 117 | 118 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7670765841199 -1.36999879607117, 36.7673984075653 -1.36823663832402) | LINESTRING Z (36.7670765841199 -1.36999879607117 0,36.7673984075653 -1.36823663832402 0)
46 | node6 -409 | 97 | node6 | 409 |  | 0.176 | 135 | 73 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7623921963995 -1.35194549133002, 36.763036432869 -1.35049720568309) | LINESTRING Z (36.7623921963995 -1.35194549133002 0,36.763036432869 -1.35049720568309 0)
47 | node10 -32027 | 98 | node10 | 32027 |  | 0.147 | 114 | 84 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7622855261742 -1.36069603276204, 36.7609651864401 -1.36078082293381) | LINESTRING Z (36.7622855261742 -1.36069603276204 0,36.7609651864401 -1.36078082293381 0)
48 | 409 -node7 | 99 | 409 | node7 |  | 0.497 | 73 | 138 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.763036432869 -1.35049720568309, 36.7644539464403 -1.3479635865548,36.7651574651 | LINESTRING Z (36.763036432869 -1.35049720568309 0,36.7644539464403 -1.3479635865548 0,36.7651574651075 -1.34656776213099 0)
49 | node1 -00462B | 100 | node1 | 00462B |  | 0.355 | 113 | 88 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7667231620065 -1.38047793835761, 36.7698813824731 -1.38001194403103) | LINESTRING Z (36.7667231620065 -1.38047793835761 0,36.7698813824731 -1.38001194403103 0)
50 | 12105 -node8 | 101 | 12105 | node8 |  | 0.091 | 142 | 139 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7618156185011 -1.35592046277368, 36.7620971077276 -1.35668690737419) | LINESTRING Z (36.7618156185011 -1.35592046277368 0,36.7620971077276 -1.35668690737419 0)
51 | node14 -460 | 102 | node14 | 460 |  | 0.098 | 118 | 99 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7670765841199 -1.36999879607117, 36.7661985846384 -1.37000010459701) | LINESTRING Z (36.7670765841199 -1.36999879607117 0,36.7661985846384 -1.37000010459701 0)
52 | node14 -32013T | 103 | node14 | 32013T |  | 0.252 | 118 | 98 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7681820421319 -1.37197221229169, 36.7670765841199 -1.36999879607117) | LINESTRING Z (36.7681820421319 -1.37197221229169 0,36.7670765841199 -1.36999879607117 0)
53 | node25 -14156 | 104 | node25 | 14156 |  | 0.051 | 130 | 112 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7649949841971 -1.36363436841892, 36.7646794846246 -1.36330388643667) | LINESTRING Z (36.7649949841971 -1.36363436841892 0,36.7646794846246 -1.36330388643667 0)
54 | node24 -node25 | 105 | node24 | node25 |  | 0.163 | 129 | 130 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7646794846246 -1.36330388643667, 36.7636846570309 -1.36223224500122) | LINESTRING Z (36.7646794846246 -1.36330388643667 0,36.7636846570309 -1.36223224500122 0)
55 | node23 -456 | 106 | node23 | 456 |  | 0.07 | 128 | 94 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7558333036587 -1.36313160563965, 36.7552123181797 -1.3632251871156) | LINESTRING Z (36.7558333036587 -1.36313160563965 0,36.7552123181797 -1.3632251871156 0)
56 | node17 -465 | 107 | node17 | 465 |  | 0.033 | 121 | 108 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.757888759798 -1.37319733022595, 36.7579264893446 -1.37349144029173) | LINESTRING Z (36.757888759798 -1.37319733022595 0,36.7579264893446 -1.37349144029173 0)
57 | node20 -node2 | 108 | node20 | node2 |  | 0.576 | 125 | 124 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7462733180924 -1.37453872997444, 36.7411357236897 -1.3751567511646) | LINESTRING Z (36.7462733180924 -1.37453872997444 0,36.7411357236897 -1.3751567511646 0)
58 | node2 -33950 | 110 | node2 | 33950 |  | 0.108 | 124 | 147 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7411357236897 -1.3751567511646, 36.7410896562047 -1.37418876869938) | LINESTRING Z (36.7411357236897 -1.3751567511646 0,36.7410896562047 -1.37418876869938 0)
59 | node2 -447 | 111 | node2 | 447 |  | 0.237 | 124 | 148 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7411357236897 -1.3751567511646, 36.7412361387439 -1.37728738234144) | LINESTRING Z (36.7411357236897 -1.3751567511646 0,36.7412361387439 -1.37728738234144 0)
60 | node4 -node5 | 113 | node4 | node5 |  | 0.16 | 133 | 134 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7603337106913 -1.35236395032121, 36.7589102901439 -1.35254987804557) | LINESTRING Z (36.7603337106913 -1.35236395032121 0,36.7589102901439 -1.35254987804557 0)
61 | node20 -node21 | 114 | node20 | node21 |  | 0.794 | 125 | 126 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7462733180924 -1.37453872997444, 36.7463050284598 -1.38080303707381,36.74715535795 | LINESTRING Z (36.7462733180924 -1.37453872997444 0,36.7463050284598 -1.38080303707381 0,36.7471553579504 -1.38099637926356 0)
62 | node4 -404 | 118 | node4 | 404 |  | 0.434 | 133 | 150 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7589102901439 -1.35254987804557, 36.7586187095724 -1.35002870712677,36.7586 | LINESTRING Z (36.7589102901439 -1.35254987804557 0,36.7586187095724 -1.35002870712677 0,36.7586065662688 -1.3493365388204 0,36.7586495558373 -1.34867344535816 0)
63 | 4001 -node3 | 119 | 4001 | node3 |  | 0.124 | 78 | 132 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7563878830746 -1.35283104378804, 36.756256521237 -1.35172476577396) | LINESTRING Z (36.7563878830746 -1.35283104378804 0,36.756256521237 -1.35172476577396 0)
64 | node3 -04058A | 120 | node3 | 04058A |  | 0.06 | 132 | 68 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7569132002294 -1.35272869876763, 36.7563878830746 -1.35283104378804) | LINESTRING Z (36.7569132002294 -1.35272869876763 0,36.7563878830746 -1.35283104378804 0)
65 | 433 -13129 | 122 | 433 | 13129 |  | 0.311 | 72 | 69 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7531188035318 -1.35326474608744, 36.7503475000925 -1.35358701297463) | LINESTRING Z (36.7531188035318 -1.35326474608744 0,36.7503475000925 -1.35358701297463 0)
66 | 136305 -13708 | 123 | 136305 | 13708 |  | 0.32 | 141 | 149 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7568232402855 -1.34692593186729, 36.7539687234416 -1.34724283485521) | LINESTRING Z (36.7568232402855 -1.34692593186729 0,36.7539687234416 -1.34724283485521 0)
67 | 04970B -node23 | 124 | 04970B | node23 |  | 0.409 | 76 | 128 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7594311309821 -1.36389019607431, 36.7558333036587 -1.36313160563965) | LINESTRING Z (36.7594311309821 -1.36389019607431 0,36.7558333036587 -1.36313160563965 0)
68 | 13546 -433 | 125 | 13546 | 433 |  | 0.193 | 70 | 72 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7548357734722 -1.35305642471318, 36.7531188035318 -1.35326474608744) | LINESTRING Z (36.7548357734722 -1.35305642471318 0,36.7531188035318 -1.35326474608744 0)
69 | 455 -04970B | 127 | 455 | 04970B |  | 0.356 | 146 | 76 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7618227067845 -1.36177241961839, 36.7594311309821 -1.36389019607431) | LINESTRING Z (36.7618227067845 -1.36177241961839 0,36.7594311309821 -1.36389019607431 0)
70 | node3 -13546 | 128 | node3 | 13546 |  | 0.175 | 132 | 70 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7563878830746 -1.35283104378804, 36.7548357734722 -1.35305642471318) | LINESTRING Z (36.7563878830746 -1.35283104378804 0,36.7548357734722 -1.35305642471318 0)
71 | 32013T -464 | 129 | 32013T | 464 |  | 0.646 | 98 | 97 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7624223632652 -1.37265521504387, 36.7681820421319 -1.37197221229169) | LINESTRING Z (36.7624223632652 -1.37265521504387 0,36.7681820421319 -1.37197221229169 0)
72 | node22 -106612 | 131 | node22 | 106612 |  | 0.017 | 127 | 62 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7555190442461 -1.35702584112019, 36.7554608025107 -1.35688558713458) | LINESTRING Z (36.7555190442461 -1.35702584112019 0,36.7554608025107 -1.35688558713458 0)
73 | node6 -node6b | 132 | node6 | node6b |  | 0.438 | 135 | 137 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7617961576617 -1.35583823096373, 36.7623921963995 -1.35194549133002) | LINESTRING Z (36.7617961576617 -1.35583823096373 0,36.7623921963995 -1.35194549133002 0)
74 | node21 -3907 | 133 | node21 | 3907 |  | 0.098 | 126 | 143 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7471553579504 -1.38099637926356, 36.7463050284598 -1.38080303707381,36.7463 | LINESTRING Z (36.7471553579504 -1.38099637926356 0,36.7463050284598 -1.38080303707381 0,36.7463032038169 -1.38080988757234 0)
75 | node6b -00454NR | 135 | node6b | 00454NR |  | 0.375 | 137 | 71 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7617961576617 -1.35583823096373, 36.7609729925618 -1.3559546392936,36.7584725839617 | LINESTRING Z (36.7617961576617 -1.35583823096373 0,36.7609729925618 -1.3559546392936 0,36.7584725839617 -1.35639817290244 0)
76 | node9 -408 | 137 | node9 | 408 |  | 0.089 | 140 | 102 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7624322359531 -1.35891324510337, 36.7616372656626 -1.35898377956509) | LINESTRING Z (36.7624322359531 -1.35891324510337 0,36.7616372656626 -1.35898377956509 0)
77 | node25 -169238 | 138 | node25 | 169238 |  | 0.02 | 130 | 77 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7646794846246 -1.36330388643667, 36.7645527914373 -1.36342505805443) | LINESTRING Z (36.7646794846246 -1.36330388643667 0,36.7645527914373 -1.36342505805443 0)
78 | 00454NR -node22 | 139 | 00454NR | node22 |  | 0.672 | 71 | 127 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7555190442461 -1.35702584112019, 36.7584725839617 -1.35639817290244,36.755519 | LINESTRING Z (36.7555190442461 -1.35702584112019 0,36.7584725839617 -1.35639817290244 0,36.7555190442461 -1.35702584112019 0)
79 | 2009 -node19 | 141 | 2009 | node19 |  | 0.326 | 105 | 123 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7612068626399 -1.37964570579744, 36.7612166137447 -1.38256040644122,36.7612165638942 | LINESTRING Z (36.7612068626399 -1.37964570579744 0,36.7612166137447 -1.38256040644122 0,36.7612165638942 -1.38254550565052 0)
80 | 450 -16370 | 142 | 450 | 16370 |  | 0.217 | 93 | 92 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7567865754473 -1.37905058253932, 36.7567183085312 -1.38099466561844) | LINESTRING Z (36.7567865754473 -1.37905058253932 0,36.7567183085312 -1.38099466561844 0)
81 | node8 -117295 | 143 | node8 | 117295 |  | 0.053 | 139 | 67 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7616185428589 -1.35672560455267, 36.7620971077276 -1.35668690737419) | LINESTRING Z (36.7616185428589 -1.35672560455267 0,36.7620971077276 -1.35668690737419 0)
82 | node18 -450 | 144 | node18 | 450 |  | 0.197 | 122 | 93 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7585500007543 -1.3788663993872, 36.7567865754473 -1.37905058253932) | LINESTRING Z (36.7585500007543 -1.3788663993872 0,36.7567865754473 -1.37905058253932 0)
83 | node11 -455 | 145 | node11 | 455 |  | 0.12 | 115 | 146 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7624931584252 -1.3609281124923, 36.7618227067845 -1.36177241961839) | LINESTRING Z (36.7624931584252 -1.3609281124923 0,36.7618227067845 -1.36177241961839 0)
84 | node24 -32287 | 176 | node24 | 32287 |  | 0.016 | 129 | 145 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7636846570309 -1.36223224500122, 36.7637952838629 -1.36213885472542) | LINESTRING Z (36.7636846570309 -1.36223224500122 0,36.7637952838629 -1.36213885472542 0)
85 | node19 -1671 | 1001 | node19 | 1671 |  | 0.262 | 123 | 104 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7612166137447 -1.38256040644122, 36.7634808969931 -1.38318627085982,36.76348 | LINESTRING Z (36.7612166137447 -1.38256040644122 0,36.7634808969931 -1.38318627085982 0,36.7634808969931 -1.38318627085982 0,36.7634808969931 -1.38318627085982 0,36.7634808969931 -1.38318627085982 0,36.7634808969931 -1.38318627085982 0,36.7634808969931 -1.38318627085982 0,36.7634808969931 -1.38318627085982 0,36.7634808969931 -1.38318627085982 0)
86 | node21 -168973 | 1002 | node21 | 168973 |  | 0.119 | 126 | 85 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7463032038169 -1.38080988757234, 36.7460346937503 -1.38184023337188) | LINESTRING Z (36.7463032038169 -1.38080988757234 0,36.7460346937503 -1.38184023337188 0)
87 | node5 -106600 | 134112 | node5 | 106600 |  | 0.222 | 134 | 61 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7603337106913 -1.35236395032121, 36.7605795763563 -1.35286426923963) | LINESTRING Z (36.7603337106913 -1.35236395032121 0,36.7605795763563 -1.35286426923963 0)
88 | node22 -175528 | 140,19 | node22 | 175528 |  | 0.02 | 127 | 79 | 80 | 0.2 | 0.4 | 3.9 | 0.2 | 0.4 | 3.9 | 0.5 | 1.7 | 1.7 | 0.487 | 1 | (36.7554793265145 -1.3571046954011, 36.7555190442461 -1.35702584112019) | LINESTRING Z (36.7554793265145 -1.3571046954011 0,36.7555190442461 -1.35702584112019 0)

## trafos
| name |  | skVA | s_nom | type | bus0 | to_bus | bus1 | from_bus | hv_bus | lv_bus | vn_lv_kv |  | vn_hv_kv | pfe | vk_percent | vkr_percent | i0_percent
0 | 00453B-K.B.C._LANGATA 0.415 | 32287 - SAIFEE PARK_MAGADI RD. | 5 | 0.005 | 5kVA 33/0.415 | 00453B-K.B.C._LANGATA 0.415 | 0 | K.B.C._LANGATA | 87 | 1 | 1 | 0.415 | 5 | 11 | 0.08 | 4 | 1 | 0.24 | 0.005
1 | 00454NR-BOGANI EAST ROAD_III 0.415 | 02037 - KENYA NATIONAL PARK_0 | 5 | 0.005 | 5kVA 33/0.415 | 00454NR-BOGANI EAST ROAD_III 0.415 | 1 | BOGANI EAST ROAD_III | 71 | 1 | 1 | 0.415 | 5 | 11 | 0.08 | 4 | 1 | 0.24 | 0.005
2 | 00462B-K.C.C.T_MBAGATHI 0.415 | 00458 - KISEMBE ROAD | 100 | 0.1 | 100kVA 33/0.415 | 00462B-K.C.C.T_MBAGATHI 0.415 | 2 | K.C.C.T_MBAGATHI | 88 | 1 | 1 | 0.415 | 100 | 11 | 0.32 | 4 | 1 | 0.24 | 0.1
3 | 04058A-BOGANI EAST ROAD_0 0.415 | 16041 - BANDA ROAD_KISEMBE | 200 | 0.2 | 200kVA 33/0.415 | 04058A-BOGANI EAST ROAD_0 0.415 | 3 | BOGANI EAST ROAD_0 | 68 | 1 | 1 | 0.415 | 200 | 11 | 0.365 | 4 | 1.2 | 0.24 | 0.2
4 | 04970B-BURHANIYA SCHOOL 0.415 | 14156 - NETWORK INTERNATIONAL | 200 | 0.2 | 200kVA 33/0.415 | 04970B-BURHANIYA SCHOOL 0.415 | 4 | BURHANIYA SCHOOL | 76 | 1 | 1 | 0.415 | 200 | 11 | 0.365 | 4 | 1.2 | 0.24 | 0.2
5 | 106600-106600 0.415 | 00459 - KISEMBE ESTATE | 100 | 0.1 | 100kVA 33/0.415 | 106600-106600 0.415 | 5 | 106600 | 61 | 1 | 1 | 0.415 | 100 | 11 | 0.32 | 4 | 1 | 0.24 | 0.1
6 | 106601-NEAR BROOKHOUSE SCHOOL 0.415 | 16370 - KIKENI DRIVE | 200 | 0.2 | 200kVA 33/0.415 | 106601-NEAR BROOKHOUSE SCHOOL 0.415 | 6 | NEAR BROOKHOUSE SCHOOL | 111 | 1 | 1 | 0.415 | 200 | 11 | 0.365 | 4 | 1.2 | 0.24 | 0.2
7 | 106612-106612 0.415 | 32013T - KISEMBE PUMP | 200 | 0.2 | 200kVA 33/0.415 | 106612-106612 0.415 | 7 | 106612 | 62 | 1 | 1 | 0.415 | 200 | 11 | 0.365 | 4 | 1.2 | 0.24 | 0.2
8 | 117295-BBROOD KENYA LIMITED 0.415 | 02189 - NDOROBO ROAD | 100 | 0.1 | 100kVA 33/0.415 | 117295-BBROOD KENYA LIMITED 0.415 | 8 | BBROOD KENYA LIMITED | 67 | 1 | 1 | 0.415 | 100 | 11 | 0.32 | 4 | 1 | 0.24 | 0.1
9 | 12105-PARK PLACE HOTEL 0.415 | 00446 - PARK VIEW_LANGATA | 200 | 0.2 | 200kVA 33/0.415 | 12105-PARK PLACE HOTEL 0.415 | 9 | PARK PLACE HOTEL | 142 | 1 | 1 | 0.415 | 200 | 11 | 0.365 | 4 | 1.2 | 0.24 | 0.2
10 | 127138-DAWAT 2 0.415 | 03907 - PARK VIEW EST._LANGATA | 200 | 0.2 | 200kVA 33/0.415 | 127138-DAWAT 2 0.415 | 10 | DAWAT 2 | 82 | 1 | 1 | 0.415 | 200 | 11 | 0.365 | 4 | 1.2 | 0.24 | 0.2
11 | 12747-APOSTLES OF JESUS 0.415 | 13073 - GATAKA WATER SUPPLY | 200 | 0.2 | 200kVA 33/0.415 | 12747-APOSTLES OF JESUS 0.415 | 11 | APOSTLES OF JESUS | 63 | 1 | 1 | 0.415 | 200 | 11 | 0.365 | 4 | 1.2 | 0.24 | 0.2
12 | 13073-GATAKA WATER SUPPLY 0.415 | 02009 - MUNDERENDU RD_LANGATA | 100 | 0.1 | 100kVA 33/0.415 | 13073-GATAKA WATER SUPPLY 0.415 | 12 | GATAKA WATER SUPPLY | 86 | 1 | 1 | 0.415 | 100 | 11 | 0.32 | 4 | 1 | 0.24 | 0.1
13 | 13129-BOGANI EAST ROAD_I 0.415 | 00456 - KIPEVU ROAD | 100 | 0.1 | 100kVA 33/0.415 | 13129-BOGANI EAST ROAD_I 0.415 | 13 | BOGANI EAST ROAD_I | 69 | 1 | 1 | 0.415 | 100 | 11 | 0.32 | 4 | 1 | 0.24 | 0.1
14 | 13546-BOGANI EAST ROAD_II 0.415 | 106601 - NEAR BROOKHOUSE SCHO | 200 | 0.2 | 200kVA 33/0.415 | 13546-BOGANI EAST ROAD_II 0.415 | 14 | BOGANI EAST ROAD_II | 70 | 1 | 1 | 0.415 | 200 | 11 | 0.365 | 4 | 1.2 | 0.24 | 0.2
15 | 13595-BANDA PREPARATORY SCH. 0.415 | 165257 - CATHOLIC UNIVERSITY | 315 | 0.315 | 315kVA 33/0.415 | 13595-BANDA PREPARATORY SCH. 0.415 | 15 | BANDA PREPARATORY SCH. | 64 | 1 | 1 | 0.415 | 315 | 11 | 1.05 | 4 | 1.325 | 0.2375 | 0.315
16 | 136305-NORKAN S.TREATMENT PLANT 0.415 | 04058A - BOGANI EAST ROAD | 15 | 0.015 | 15kVA 33/0.415 | 136305-NORKAN S.TREATMENT PLANT 0.415 | 16 | NORKAN S.TREATMENT PLANT | 141 | 1 | 1 | 0.415 | 15 | 11 | 0.08 | 4 | 1 | 0.24 | 0.015
17 | 13708-ST. AQUINAS SEMINARY 0.415 | 00457 - BANDA ROAD_KISEMBE_II | 200 | 0.2 | 200kVA 33/0.415 | 13708-ST. AQUINAS SEMINARY 0.415 | 17 | ST. AQUINAS SEMINARY | 149 | 1 | 1 | 0.415 | 200 | 11 | 0.365 | 4 | 1.2 | 0.24 | 0.2
18 | 14156-NETWORK INTERNATIONAL 0.415 | 00409 - BOGANI ROAD | 50 | 0.05 | 50kVA 33/0.415 | 14156-NETWORK INTERNATIONAL 0.415 | 18 | NETWORK INTERNATIONAL | 112 | 1 | 1 | 0.415 | 50 | 11 | 0.13 | 4 | 1 | 0.24 | 0.05
19 | 16041-BANDA ROAD_KISEMBE 0.415 | 12105 - PARK PLACE HOTEL | 200 | 0.2 | 200kVA 33/0.415 | 16041-BANDA ROAD_KISEMBE 0.415 | 19 | BANDA ROAD_KISEMBE | 65 | 1 | 1 | 0.415 | 200 | 11 | 0.365 | 4 | 1.2 | 0.24 | 0.2
20 | 16253-BROOKE HOUSE SCHOOL_0 0.415 | 13129 - BOGANI EAST ROAD | 200 | 0.2 | 200kVA 33/0.415 | 16253-BROOKE HOUSE SCHOOL_0 0.415 | 20 | BROOKE HOUSE SCHOOL_0 | 74 | 1 | 1 | 0.415 | 200 | 11 | 0.365 | 4 | 1.2 | 0.24 | 0.2
21 | 16370-KIKENI DRIVE 0.415 | 13546 - BOGANI EAST ROAD | 315 | 0.315 | 315kVA 33/0.415 | 16370-KIKENI DRIVE 0.415 | 21 | KIKENI DRIVE | 92 | 1 | 1 | 0.415 | 315 | 11 | 1.05 | 4 | 1.325 | 0.2375 | 0.315
22 | 165257-CATHOLIC UNIVERSITY_I 0.415 | 13595 - BANDA PREPARATORY SCH. | 100 | 0.1 | 100kVA 33/0.415 | 165257-CATHOLIC UNIVERSITY_I 0.415 | 22 | CATHOLIC UNIVERSITY_I | 80 | 1 | 1 | 0.415 | 100 | 11 | 0.32 | 4 | 1 | 0.24 | 0.1
23 | 1670-MUNDERENDU ROAD_LANGATA 0.415 | NO.NO.1 - CATHOLIC UNIVERSITY | 630 | 0.63 | 630kVA 33/0.415 | 1670-MUNDERENDU ROAD_LANGATA 0.415 | 23 | MUNDERENDU ROAD_LANGATA | 106 | 1 | 1 | 0.415 | 630 | 11 | 1.18 | 4 | 1.0794 | 0.1873 | 0.63
24 | 1671-MUHUTI ROAD_LANGATA 0.415 | 16253 - BROOKE HOUSE SCHOOL | 315 | 0.315 | 315kVA 33/0.415 | 1671-MUHUTI ROAD_LANGATA 0.415 | 24 | MUHUTI ROAD_LANGATA | 104 | 1 | 1 | 0.415 | 315 | 11 | 1.05 | 4 | 1.325 | 0.2375 | 0.315
25 | 168973-GATAKA BOREHOLE 0.415 | 00464 - KISEMBE ESTATE | 200 | 0.2 | 200kVA 33/0.415 | 168973-GATAKA BOREHOLE 0.415 | 25 | GATAKA BOREHOLE | 85 | 1 | 1 | 0.415 | 200 | 11 | 0.365 | 4 | 1.2 | 0.24 | 0.2
26 | 169238-CAMBRIDGE 0.415 | 00450 - KIKENI ROAD | 200 | 0.2 | 200kVA 33/0.415 | 169238-CAMBRIDGE 0.415 | 26 | CAMBRIDGE | 77 | 1 | 1 | 0.415 | 200 | 11 | 0.365 | 4 | 1.2 | 0.24 | 0.2
27 | 175528-CATHOLIC UNIVERSITY OF E A 0.415 | 45161 - DAWAT E HADIYA | 315 | 0.315 | 315kVA 33/0.415 | 175528-CATHOLIC UNIVERSITY OF E A 0.415 | 27 | CATHOLIC UNIVERSITY OF E A | 79 | 1 | 1 | 0.415 | 315 | 11 | 1.05 | 4 | 1.325 | 0.2375 | 0.315
28 | 1956-BROOKE HOUSE SCHOOL_I 0.415 | 00455 - SAIFEE PARK_MAGADI RD. | 315 | 0.315 | 315kVA 33/0.415 | 1956-BROOKE HOUSE SCHOOL_I 0.415 | 28 | BROOKE HOUSE SCHOOL_I | 75 | 1 | 1 | 0.415 | 315 | 11 | 1.05 | 4 | 1.325 | 0.2375 | 0.315
29 | 2009-MUNDERENDU RD_LANGATA 0.415 | 01671 - MUHUTI ROAD_LANGATA | 50 | 0.05 | 50kVA 33/0.415 | 2009-MUNDERENDU RD_LANGATA 0.415 | 29 | MUNDERENDU RD_LANGATA | 105 | 1 | 1 | 0.415 | 50 | 11 | 0.13 | 4 | 1 | 0.24 | 0.05
30 | 2037-KENYA NATIONAL PARK_0 0.415 | 33950 - SIMBA HILL ROAD | 100 | 0.1 | 100kVA 33/0.415 | 2037-KENYA NATIONAL PARK_0 0.415 | 30 | KENYA NATIONAL PARK_0 | 91 | 1 | 1 | 0.415 | 100 | 11 | 0.32 | 4 | 1 | 0.24 | 0.1
31 | 2038-KENYA NATIONAL PARK 0.415 | 00447 - SIMBA HILL ROAD | 200 | 0.2 | 200kVA 33/0.415 | 2038-KENYA NATIONAL PARK 0.415 | 31 | KENYA NATIONAL PARK | 90 | 1 | 1 | 0.415 | 200 | 11 | 0.365 | 4 | 1.2 | 0.24 | 0.2
32 | 2189-NDOROBO ROAD_0 0.415 | 00463 - K.W.S_B/HOLE | 200 | 0.2 | 200kVA 33/0.415 | 2189-NDOROBO ROAD_0 0.415 | 32 | NDOROBO ROAD_0 | 107 | 1 | 1 | 0.415 | 200 | 11 | 0.365 | 4 | 1.2 | 0.24 | 0.2
33 | 32013T-KISEMBE PUMP_0 0.415 | 02038 - KENYA NATIONAL PARK | 100 | 0.1 | 100kVA 33/0.415 | 32013T-KISEMBE PUMP_0 0.415 | 33 | KISEMBE PUMP_0 | 98 | 1 | 1 | 0.415 | 100 | 11 | 0.32 | 4 | 1 | 0.24 | 0.1
34 | 32027-DEWAT E. HADIYA_I 0.415 | 01670 - MUNDERENDU ROAD_LANGA | 200 | 0.2 | 200kVA 33/0.415 | 32027-DEWAT E. HADIYA_I 0.415 | 34 | DEWAT E. HADIYA_I | 84 | 1 | 1 | 0.415 | 200 | 11 | 0.365 | 4 | 1.2 | 0.24 | 0.2
35 | 32287-SAIFEE PARK_MAGADI RD_0 0.415 | 00454NR - BOGANI EAST ROAD | 100 | 0.1 | 100kVA 33/0.415 | 32287-SAIFEE PARK_MAGADI RD_0 0.415 | 35 | SAIFEE PARK_MAGADI RD_0 | 145 | 1 | 1 | 0.415 | 100 | 11 | 0.32 | 4 | 1 | 0.24 | 0.1
36 | 33950-SIMBA HILL ROAD_0 0.415 | 00462B - K.C.C.T_MBAGATHI | 630 | 0.63 | 630kVA 33/0.415 | 33950-SIMBA HILL ROAD_0 0.415 | 36 | SIMBA HILL ROAD_0 | 147 | 1 | 1 | 0.415 | 630 | 11 | 1.18 | 4 | 1.0794 | 0.1873 | 0.63
37 | 3907-PARK VIEW EST._LANGATA 0.415 | 127138 - DAWAT 2 | 5 | 0.005 | 200kVA 33/0.415 | 3907-PARK VIEW EST._LANGATA 0.415 | 37 | PARK VIEW EST._LANGATA | 143 | 1 | 1 | 0.415 | 5 | 11 | 0.365 | 4 | 1.2 | 0.24 | 0.005
38 | 4001-CATHOLIC UNIVERSITY_0 0.415 | 01956 - BROOKE HOUSE SCHOOL | 200 | 0.2 | 200kVA 33/0.415 | 4001-CATHOLIC UNIVERSITY_0 0.415 | 38 | CATHOLIC UNIVERSITY_0 | 78 | 1 | 1 | 0.415 | 200 | 11 | 0.365 | 4 | 1.2 | 0.24 | 0.2
39 | 404-ST.THOMAS SEMINARY 0.415 | 106612 - 106612 | 100 | 0.1 | 100kVA 33/0.415 | 404-ST.THOMAS SEMINARY 0.415 | 39 | ST.THOMAS SEMINARY | 150 | 1 | 1 | 0.415 | 100 | 11 | 0.32 | 4 | 1 | 0.24 | 0.1
40 | 408-MAGADI ROAD 0.415 | 12747 - APOSTLES OF JESUS | 1000 | 1 | 1000kVA 33/0.415 | 408-MAGADI ROAD 0.415 | 40 | MAGADI ROAD | 102 | 1 | 1 | 0.415 | 1000 | 11 | 1.18 | 6 | 1.0794 | 0.1873 | 1
41 | 409-BOGANI ROAD_V 0.415 | 04001 - CATHOLIC UNIVERSITY | 315 | 0.315 | 315kVA 33/0.415 | 409-BOGANI ROAD_V 0.415 | 41 | BOGANI ROAD_V | 73 | 1 | 1 | 0.415 | 315 | 11 | 1.05 | 4 | 1.325 | 0.2375 | 0.315
42 | 433-BOGANI EAST ROAD_IV 0.415 | 168973 - GATAKA BOREHOLE | 5 | 0.005 | 200kVA 33/0.415 | 433-BOGANI EAST ROAD_IV 0.415 | 42 | BOGANI EAST ROAD_IV | 72 | 1 | 1 | 0.415 | 5 | 11 | 0.365 | 4 | 1.2 | 0.24 | 0.005
43 | 446-PARK VIEW_LANGATA 0.415 | 32027 - DEWAT E. HADIYA | 315 | 0.315 | 315kVA 33/0.415 | 446-PARK VIEW_LANGATA 0.415 | 43 | PARK VIEW_LANGATA | 144 | 1 | 1 | 0.415 | 315 | 11 | 1.05 | 4 | 1.325 | 0.2375 | 0.315
44 | 447-SIMBA HILL ROAD_I 0.415 | 00465 - NDOROBO ROAD | 50 | 0.05 | 50kVA 33/0.415 | 447-SIMBA HILL ROAD_I 0.415 | 44 | SIMBA HILL ROAD_I | 148 | 1 | 1 | 0.415 | 50 | 11 | 0.13 | 4 | 1 | 0.24 | 0.05
45 | 449-KISEMBE EAST 0.415 | 00433 - BOGANI EAST ROAD | 100 | 0.1 | 100kVA 33/0.415 | 449-KISEMBE EAST 0.415 | 45 | KISEMBE EAST | 95 | 1 | 1 | 0.415 | 100 | 11 | 0.32 | 4 | 1 | 0.24 | 0.1
46 | 450-KIKENI ROAD 0.415 | 00460 - KISEMBE PUMP | 315 | 0.315 | 315kVA 33/0.415 | 450-KIKENI ROAD 0.415 | 46 | KIKENI ROAD | 93 | 1 | 1 | 0.415 | 315 | 11 | 1.05 | 4 | 1.325 | 0.2375 | 0.315
47 | 45161-DAWAT E HADIYA_0 0.415 | 117295 - BBROOD KENYA LIMITED | 200 | 0.2 | 200kVA 33/0.415 | 45161-DAWAT E HADIYA_0 0.415 | 47 | DAWAT E HADIYA_0 | 83 | 1 | 1 | 0.415 | 200 | 11 | 0.365 | 4 | 1.2 | 0.24 | 0.2
48 | 455-SAIFEE PARK_MAGADI RD_I 0.415 | 00467 - NDOROBO ROAD | 200 | 0.2 | 200kVA 33/0.415 | 455-SAIFEE PARK_MAGADI RD_I 0.415 | 48 | SAIFEE PARK_MAGADI RD_I | 146 | 1 | 1 | 0.415 | 200 | 11 | 0.365 | 4 | 1.2 | 0.24 | 0.2
49 | 456-KIPEVU ROAD 0.415 | 00449 - KISEMBE EAST | 200 | 0.2 | 200kVA 33/0.415 | 456-KIPEVU ROAD 0.415 | 49 | KIPEVU ROAD | 94 | 1 | 1 | 0.415 | 200 | 11 | 0.365 | 4 | 1.2 | 0.24 | 0.2
50 | 457-BANDA ROAD_KISEMBE_II 0.415 | 00461 - MMU | 5 | 0.005 | 5kVA 33/0.415 | 457-BANDA ROAD_KISEMBE_II 0.415 | 50 | BANDA ROAD_KISEMBE_II | 66 | 1 | 1 | 0.415 | 5 | 11 | 0.08 | 4 | 1 | 0.24 | 0.005
51 | 458-KISEMBE ROAD 0.415 | 00466 - NDOROBO ROAD | 25 | 0.025 | 25kVA 33/0.415 | 458-KISEMBE ROAD 0.415 | 51 | KISEMBE ROAD | 100 | 1 | 1 | 0.415 | 25 | 11 | 0.1 | 4 | 1 | 0.24 | 0.025
52 | 459-KISEMBE ESTATE_0 0.415 | 00404 - ST.THOMAS SEMINARY | 100 | 0.1 | 100kVA 33/0.415 | 459-KISEMBE ESTATE_0 0.415 | 52 | KISEMBE ESTATE_0 | 96 | 1 | 1 | 0.415 | 100 | 11 | 0.32 | 4 | 1 | 0.24 | 0.1
53 | 460-KISEMBE PUMP_I 0.415 | 04970B - BURHANIYA SCHOOL | 1000 | 1 | 1000kVA 33/0.415 | 460-KISEMBE PUMP_I 0.415 | 53 | KISEMBE PUMP_I | 99 | 1 | 1 | 0.415 | 1000 | 11 | 1.18 | 6 | 1.0794 | 0.1873 | 1
54 | 461-MMU 0.415 | 00453B - K.B.C._LANGATA | 315 | 0.315 | 315kVA 33/0.415 | 461-MMU 0.415 | 54 | MMU | 103 | 1 | 1 | 0.415 | 315 | 11 | 1.05 | 4 | 1.325 | 0.2375 | 0.315
55 | 463-K.W.S_B/HOLE 0.415 | 175528 - CATHOLIC UNIVERSITY | 100 | 0.1 | 100kVA 33/0.415 | 463-K.W.S_B/HOLE 0.415 | 55 | K.W.S_B/HOLE | 89 | 1 | 1 | 0.415 | 100 | 11 | 0.32 | 4 | 1 | 0.24 | 0.1
56 | 464-KISEMBE ESTATE_I 0.415 | 136305 - NORKAN S.TREATMENT P | 200 | 0.2 | 200kVA 33/0.415 | 464-KISEMBE ESTATE_I 0.415 | 56 | KISEMBE ESTATE_I | 97 | 1 | 1 | 0.415 | 200 | 11 | 0.365 | 4 | 1.2 | 0.24 | 0.2
57 | 465-NDOROBO ROAD_I 0.415 | 169238 - CAMBRIDGE | 1000 | 1 | 1000kVA 33/0.415 | 465-NDOROBO ROAD_I 0.415 | 57 | NDOROBO ROAD_I | 108 | 1 | 1 | 0.415 | 1000 | 11 | 1.18 | 6 | 1.0794 | 0.1873 | 1
58 | 466-NDOROBO ROAD_III 0.415 | 00408 - MAGADI ROAD | 200 | 0.2 | 200kVA 33/0.415 | 466-NDOROBO ROAD_III 0.415 | 58 | NDOROBO ROAD_III | 110 | 1 | 1 | 0.415 | 200 | 11 | 0.365 | 4 | 1.2 | 0.24 | 0.2
59 | 467-NDOROBO ROAD_II 0.415 | 106600 - 106600 | 315 | 0.315 | 315kVA 33/0.415 | 467-NDOROBO ROAD_II 0.415 | 59 | NDOROBO ROAD_II | 109 | 1 | 1 | 0.415 | 315 | 11 | 1.05 | 4 | 1.325 | 0.2375 | 0.315
60 | NO.NO.1-CATHOLIC UNIVERSITY 0.415 | 13708 - ST. AQUINAS SEMINARY | 100 | 0.1 | 100kVA 33/0.415 | NO.NO.1-CATHOLIC UNIVERSITY 0.415 | 60 | CATHOLIC UNIVERSITY_II | 81 | 1 | 1 | 0.415 | 100 | 11 | 0.32 | 4 | 1 | 0.24 | 0.1

## load
| name | bus_id |  | bus_name | bus | in_service | pf | s_nom | p_set | q_set | % Motor Load | % LRC | X/R | scaling
0 | 00453B-K.B.C._LANGATA 0.415 | 32287 0.415 | 00453B 0.415 | 00453B-K.B.C._LANGATA 0.415 | 0 | 1 | 0.85 | 0.005 | 0.002125 | 0.001317 | 10 |  |  | 0.5 | scaling factor | 0.5
1 | 00454NR-BOGANI EAST ROAD_III 0.415 | 2037 0.415 | 00454NR 0.415 | 00454NR-BOGANI EAST ROAD_III 0.415 | 1 | 1 | 0.85 | 0.005 | 0.002125 | 0.001317 | 10 |  |  | 0.5
2 | 00462B-K.C.C.T_MBAGATHI 0.415 | 458 0.415 | 00462B 0.415 | 00462B-K.C.C.T_MBAGATHI 0.415 | 2 | 1 | 0.85 | 0.1 | 0.0425 | 0.026339 | 10 |  |  | 0.5
3 | 04058A-BOGANI EAST ROAD_0 0.415 | 16041 0.415 | 04058A 0.415 | 04058A-BOGANI EAST ROAD_0 0.415 | 3 | 1 | 0.85 | 0.2 | 0.085 | 0.052678 | 10 |  |  | 0.5
4 | 04970B-BURHANIYA SCHOOL 0.415 | 14156 0.415 | 04970B 0.415 | 04970B-BURHANIYA SCHOOL 0.415 | 4 | 1 | 0.85 | 0.2 | 0.085 | 0.052678 | 10 |  |  | 0.5
5 | 106600-106600 0.415 | 459 0.415 | 106600 0.415 | 106600-106600 0.415 | 5 | 1 | 0.85 | 0.1 | 0.0425 | 0.026339 | 10 |  |  | 0.5
6 | 106601-NEAR BROOKHOUSE SCHOOL 0.415 | 16370 0.415 | 106601 0.415 | 106601-NEAR BROOKHOUSE SCHOOL 0.415 | 6 | 1 | 0.85 | 0.2 | 0.085 | 0.052678 | 10 |  |  | 0.5
7 | 106612-106612 0.415 | 32013T 0.415 | 106612 0.415 | 106612-106612 0.415 | 7 | 1 | 0.85 | 0.2 | 0.085 | 0.052678 | 10 |  |  | 0.5
8 | 117295-BBROOD KENYA LIMITED 0.415 | 2189 0.415 | 117295 0.415 | 117295-BBROOD KENYA LIMITED 0.415 | 8 | 1 | 0.85 | 0.1 | 0.0425 | 0.026339 | 10 |  |  | 0.5
9 | 12105-PARK PLACE HOTEL 0.415 | 446 0.415 | 12105 0.415 | 12105-PARK PLACE HOTEL 0.415 | 9 | 1 | 0.85 | 0.2 | 0.085 | 0.052678 | 10 |  |  | 0.5
10 | 127138-DAWAT 2 0.415 | 3907 0.415 | 127138 0.415 | 127138-DAWAT 2 0.415 | 10 | 1 | 0.85 | 0.2 | 0.085 | 0.052678 | 10 |  |  | 0.5
11 | 12747-APOSTLES OF JESUS 0.415 | 13073 0.415 | 12747 0.415 | 12747-APOSTLES OF JESUS 0.415 | 11 | 1 | 0.85 | 0.2 | 0.085 | 0.052678 | 10 |  |  | 0.5
12 | 13073-GATAKA WATER SUPPLY 0.415 | 2009 0.415 | 13073 0.415 | 13073-GATAKA WATER SUPPLY 0.415 | 12 | 1 | 0.85 | 0.1 | 0.0425 | 0.026339 | 10 |  |  | 0.5
13 | 13129-BOGANI EAST ROAD_I 0.415 | 456 0.415 | 13129 0.415 | 13129-BOGANI EAST ROAD_I 0.415 | 13 | 1 | 0.85 | 0.1 | 0.0425 | 0.026339 | 10 |  |  | 0.5
14 | 13546-BOGANI EAST ROAD_II 0.415 | 106601 0.415 | 13546 0.415 | 13546-BOGANI EAST ROAD_II 0.415 | 14 | 1 | 0.85 | 0.2 | 0.085 | 0.052678 | 10 |  |  | 0.5
15 | 13595-BANDA PREPARATORY SCH. 0.415 | 165257 0.415 | 13595 0.415 | 13595-BANDA PREPARATORY SCH. 0.415 | 15 | 1 | 0.85 | 0.315 | 0.13387 | 0.082968 | 10 |  |  | 0.5
16 | 136305-NORKAN S.TREATMENT PLANT 0.415 | 04058A 0.415 | 136305 0.415 | 136305-NORKAN S.TREATMENT PLANT 0.415 | 16 | 1 | 0.85 | 0.015 | 0.006375 | 0.0039509 | 10 |  |  | 0.5
17 | 13708-ST. AQUINAS SEMINARY 0.415 | 457 0.415 | 13708 0.415 | 13708-ST. AQUINAS SEMINARY 0.415 | 17 | 1 | 0.85 | 0.2 | 0.085 | 0.052678 | 10 |  |  | 0.5
18 | 14156-NETWORK INTERNATIONAL 0.415 | 409 0.415 | 14156 0.415 | 14156-NETWORK INTERNATIONAL 0.415 | 18 | 1 | 0.85 | 0.05 | 0.02125 | 0.01317 | 10 |  |  | 0.5
19 | 16041-BANDA ROAD_KISEMBE 0.415 | 12105 0.415 | 16041 0.415 | 16041-BANDA ROAD_KISEMBE 0.415 | 19 | 1 | 0.85 | 0.2 | 0.085 | 0.052678 | 10 |  |  | 0.5
20 | 16253-BROOKE HOUSE SCHOOL_0 0.415 | 13129 0.415 | 16253 0.415 | 16253-BROOKE HOUSE SCHOOL_0 0.415 | 20 | 1 | 0.85 | 0.2 | 0.085 | 0.052678 | 10 |  |  | 0.5
21 | 16370-KIKENI DRIVE 0.415 | 13546 0.415 | 16370 0.415 | 16370-KIKENI DRIVE 0.415 | 21 | 1 | 0.85 | 0.315 | 0.13387 | 0.082968 | 10 |  |  | 0.5
22 | 165257-CATHOLIC UNIVERSITY_I 0.415 | 13595 0.415 | 165257 0.415 | 165257-CATHOLIC UNIVERSITY_I 0.415 | 22 | 1 | 0.85 | 0.1 | 0.0425 | 0.026339 | 10 |  |  | 0.5
23 | 1670-MUNDERENDU ROAD_LANGATA 0.415 | NO.NO.1 0.415 | 1670 0.415 | 1670-MUNDERENDU ROAD_LANGATA 0.415 | 23 | 1 | 0.85 | 0.63 | 0.26775 | 0.16594 | 10 |  |  | 0.5
24 | 1671-MUHUTI ROAD_LANGATA 0.415 | 16253 0.415 | 1671 0.415 | 1671-MUHUTI ROAD_LANGATA 0.415 | 24 | 1 | 0.85 | 0.315 | 0.13387 | 0.082968 | 10 |  |  | 0.5
25 | 168973-GATAKA BOREHOLE 0.415 | 464 0.415 | 168973 0.415 | 168973-GATAKA BOREHOLE 0.415 | 25 | 1 | 0.85 | 0.2 | 0.085 | 0.052678 | 10 |  |  | 0.5
26 | 169238-CAMBRIDGE 0.415 | 450 0.415 | 169238 0.415 | 169238-CAMBRIDGE 0.415 | 26 | 1 | 0.85 | 0.2 | 0.085 | 0.052678 | 10 |  |  | 0.5
27 | 175528-CATHOLIC UNIVERSITY OF E A 0.415 | 45161 0.415 | 175528 0.415 | 175528-CATHOLIC UNIVERSITY OF E A 0.415 | 27 | 1 | 0.85 | 0.315 | 0.13387 | 0.082968 | 10 |  |  | 0.5
28 | 1956-BROOKE HOUSE SCHOOL_I 0.415 | 455 0.415 | 1956 0.415 | 1956-BROOKE HOUSE SCHOOL_I 0.415 | 28 | 1 | 0.85 | 0.315 | 0.13387 | 0.082968 | 10 |  |  | 0.5
29 | 2009-MUNDERENDU RD_LANGATA 0.415 | 1671 0.415 | 2009 0.415 | 2009-MUNDERENDU RD_LANGATA 0.415 | 29 | 1 | 0.85 | 0.05 | 0.02125 | 0.01317 | 10 |  |  | 0.5
30 | 2037-KENYA NATIONAL PARK_0 0.415 | 33950 0.415 | 2037 0.415 | 2037-KENYA NATIONAL PARK_0 0.415 | 30 | 1 | 0.85 | 0.1 | 0.0425 | 0.026339 | 10 |  |  | 0.5
31 | 2038-KENYA NATIONAL PARK 0.415 | 447 0.415 | 2038 0.415 | 2038-KENYA NATIONAL PARK 0.415 | 31 | 1 | 0.85 | 0.2 | 0.085 | 0.052678 | 10 |  |  | 0.5
32 | 2189-NDOROBO ROAD_0 0.415 | 463 0.415 | 2189 0.415 | 2189-NDOROBO ROAD_0 0.415 | 32 | 1 | 0.85 | 0.2 | 0.085 | 0.052678 | 10 |  |  | 0.5
33 | 32013T-KISEMBE PUMP_0 0.415 | 2038 0.415 | 32013T 0.415 | 32013T-KISEMBE PUMP_0 0.415 | 33 | 1 | 0.85 | 0.1 | 0.0425 | 0.026339 | 10 |  |  | 0.5
34 | 32027-DEWAT E. HADIYA_I 0.415 | 1670 0.415 | 32027 0.415 | 32027-DEWAT E. HADIYA_I 0.415 | 34 | 1 | 0.85 | 0.2 | 0.085 | 0.052678 | 10 |  |  | 0.5
35 | 32287-SAIFEE PARK_MAGADI RD_0 0.415 | 00454NR 0.415 | 32287 0.415 | 32287-SAIFEE PARK_MAGADI RD_0 0.415 | 35 | 1 | 0.85 | 0.1 | 0.0425 | 0.026339 | 10 |  |  | 0.5
36 | 33950-SIMBA HILL ROAD_0 0.415 | 00462B 0.415 | 33950 0.415 | 33950-SIMBA HILL ROAD_0 0.415 | 36 | 1 | 0.85 | 0.63 | 0.26775 | 0.16594 | 10 |  |  | 0.5
37 | 3907-PARK VIEW EST._LANGATA 0.415 | 127138 0.415 | 3907 0.415 | 3907-PARK VIEW EST._LANGATA 0.415 | 37 | 1 | 0.85 | 0.005 | 0.002125 | 0.001317 | 10 |  |  | 0.5
38 | 4001-CATHOLIC UNIVERSITY_0 0.415 | 1956 0.415 | 4001 0.415 | 4001-CATHOLIC UNIVERSITY_0 0.415 | 38 | 1 | 0.85 | 0.2 | 0.085 | 0.052678 | 10 |  |  | 0.5
39 | 404-ST.THOMAS SEMINARY 0.415 | 106612 0.415 | 404 0.415 | 404-ST.THOMAS SEMINARY 0.415 | 39 | 1 | 0.85 | 0.1 | 0.0425 | 0.026339 | 10 |  |  | 0.5
40 | 408-MAGADI ROAD 0.415 | 12747 0.415 | 408 0.415 | 408-MAGADI ROAD 0.415 | 40 | 1 | 0.85 | 1 | 0.425 | 0.26339 | 10 |  |  | 0.5
41 | 409-BOGANI ROAD_V 0.415 | 4001 0.415 | 409 0.415 | 409-BOGANI ROAD_V 0.415 | 41 | 1 | 0.85 | 0.315 | 0.13387 | 0.082968 | 10 |  |  | 0.5
42 | 433-BOGANI EAST ROAD_IV 0.415 | 168973 0.415 | 433 0.415 | 433-BOGANI EAST ROAD_IV 0.415 | 42 | 1 | 0.85 | 0.005 | 0.002125 | 0.001317 | 10 |  |  | 0.5
43 | 446-PARK VIEW_LANGATA 0.415 | 32027 0.415 | 446 0.415 | 446-PARK VIEW_LANGATA 0.415 | 43 | 1 | 0.85 | 0.315 | 0.13387 | 0.082968 | 10 |  |  | 0.5
44 | 447-SIMBA HILL ROAD_I 0.415 | 465 0.415 | 447 0.415 | 447-SIMBA HILL ROAD_I 0.415 | 44 | 1 | 0.85 | 0.05 | 0.02125 | 0.01317 | 10 |  |  | 0.5
45 | 449-KISEMBE EAST 0.415 | 433 0.415 | 449 0.415 | 449-KISEMBE EAST 0.415 | 45 | 1 | 0.85 | 0.1 | 0.0425 | 0.026339 | 10 |  |  | 0.5
46 | 450-KIKENI ROAD 0.415 | 460 0.415 | 450 0.415 | 450-KIKENI ROAD 0.415 | 46 | 1 | 0.85 | 0.315 | 0.13387 | 0.082968 | 10 |  |  | 0.5
47 | 45161-DAWAT E HADIYA_0 0.415 | 117295 0.415 | 45161 0.415 | 45161-DAWAT E HADIYA_0 0.415 | 47 | 1 | 0.85 | 0.2 | 0.085 | 0.052678 | 10 |  |  | 0.5
48 | 455-SAIFEE PARK_MAGADI RD_I 0.415 | 467 0.415 | 455 0.415 | 455-SAIFEE PARK_MAGADI RD_I 0.415 | 48 | 1 | 0.85 | 0.2 | 0.085 | 0.052678 | 10 |  |  | 0.5
49 | 456-KIPEVU ROAD 0.415 | 449 0.415 | 456 0.415 | 456-KIPEVU ROAD 0.415 | 49 | 1 | 0.85 | 0.2 | 0.085 | 0.052678 | 10 |  |  | 0.5
50 | 457-BANDA ROAD_KISEMBE_II 0.415 | 461 0.415 | 457 0.415 | 457-BANDA ROAD_KISEMBE_II 0.415 | 50 | 1 | 0.85 | 0.005 | 0.002125 | 0.001317 | 10 |  |  | 0.5
51 | 458-KISEMBE ROAD 0.415 | 466 0.415 | 458 0.415 | 458-KISEMBE ROAD 0.415 | 51 | 1 | 0.85 | 0.025 | 0.010625 | 0.0065848 | 10 |  |  | 0.5
52 | 459-KISEMBE ESTATE_0 0.415 | 404 0.415 | 459 0.415 | 459-KISEMBE ESTATE_0 0.415 | 52 | 1 | 0.85 | 0.1 | 0.0425 | 0.026339 | 10 |  |  | 0.5
53 | 460-KISEMBE PUMP_I 0.415 | 04970B 0.415 | 460 0.415 | 460-KISEMBE PUMP_I 0.415 | 53 | 1 | 0.85 | 1 | 0.425 | 0.26339 | 10 |  |  | 0.5
54 | 461-MMU 0.415 | 00453B 0.415 | 461 0.415 | 461-MMU 0.415 | 54 | 1 | 0.85 | 0.315 | 0.13387 | 0.082968 | 10 |  |  | 0.5
55 | 463-K.W.S_B/HOLE 0.415 | 175528 0.415 | 463 0.415 | 463-K.W.S_B/HOLE 0.415 | 55 | 1 | 0.85 | 0.1 | 0.0425 | 0.026339 | 10 |  |  | 0.5
56 | 464-KISEMBE ESTATE_I 0.415 | 136305 0.415 | 464 0.415 | 464-KISEMBE ESTATE_I 0.415 | 56 | 1 | 0.85 | 0.2 | 0.085 | 0.052678 | 10 |  |  | 0.5
57 | 465-NDOROBO ROAD_I 0.415 | 169238 0.415 | 465 0.415 | 465-NDOROBO ROAD_I 0.415 | 57 | 1 | 0.85 | 1 | 0.425 | 0.26339 | 10 |  |  | 0.5
58 | 466-NDOROBO ROAD_III 0.415 | 408 0.415 | 466 0.415 | 466-NDOROBO ROAD_III 0.415 | 58 | 1 | 0.85 | 0.2 | 0.085 | 0.052678 | 10 |  |  | 0.5
59 | 467-NDOROBO ROAD_II 0.415 | 106600 0.415 | 467 0.415 | 467-NDOROBO ROAD_II 0.415 | 59 | 1 | 0.85 | 0.315 | 0.13387 | 0.082968 | 10 |  |  | 0.5
60 | NO.NO.1-CATHOLIC UNIVERSITY 0.415 | 13708 0.415 | NO.NO.1 0.415 | NO.NO.1-CATHOLIC UNIVERSITY 0.415 | 60 | 1 | 0.85 | 0.1 | 0.0425 | 0.026339 | 10 |  |  | 0.5

## bus_geodata
| x | y | coords
0 | 36.7471 | -1.3571
1 | 36.7585 | -1.3564
2 | 36.7667 | -1.3805
3 | 36.7569 | -1.3527
4 | 36.7594 | -1.3639
5 | 36.7606 | -1.3529
6 | 36.7621 | -1.3471
7 | 36.7555 | -1.3569
8 | 36.7616 | -1.3567
9 | 36.7618 | -1.3559
10 | 36.7546 | -1.361
11 | 36.7577 | -1.3433
12 | 36.749 | -1.3815
13 | 36.7503 | -1.3536
14 | 36.7548 | -1.3531
15 | 36.7666 | -1.3662
16 | 36.7568 | -1.3469
17 | 36.754 | -1.3472
18 | 36.765 | -1.3636
19 | 36.7566 | -1.3695
20 | 36.7654 | -1.346
21 | 36.7567 | -1.381
22 | 36.7579 | -1.35
23 | 36.7645 | -1.3782
24 | 36.7635 | -1.3832
25 | 36.746 | -1.3818
26 | 36.7646 | -1.3634
27 | 36.7555 | -1.3571
28 | 36.7633 | -1.3466
29 | 36.7612 | -1.3796
30 | 36.7749 | -1.3786
31 | 36.7673 | -1.3638
32 | 36.7603 | -1.3755
33 | 36.7682 | -1.372
34 | 36.761 | -1.3608
35 | 36.7638 | -1.3621
36 | 36.7411 | -1.3742
37 | 36.7472 | -1.381
38 | 36.7563 | -1.3517
39 | 36.7586 | -1.3487
40 | 36.7616 | -1.359
41 | 36.763 | -1.3505
42 | 36.7531 | -1.3533
43 | 36.7466 | -1.3745
44 | 36.7412 | -1.3773
45 | 36.7505 | -1.3741
46 | 36.7568 | -1.3791
47 | 36.7566 | -1.3614
48 | 36.7618 | -1.3618
49 | 36.7552 | -1.3632
50 | 36.7576 | -1.3683
51 | 36.7608 | -1.3681
52 | 36.7635 | -1.3679
53 | 36.7662 | -1.37
54 | 36.7682 | -1.3763
55 | 36.7733 | -1.3796
56 | 36.7624 | -1.3727
57 | 36.7579 | -1.3735
58 | 36.7582 | -1.3758
59 | 36.7587 | -1.38
60 | 36.7563 | -1.3508
61 | 36.7606 | -1.3529
62 | 36.7749 | -1.3786
63 | 36.7577 | -1.3433
64 | 36.7666 | -1.3662
65 | 36.7566 | -1.3695
66 | 36.7576 | -1.3683
67 | 36.7616 | -1.3567
68 | 36.7569 | -1.3527
69 | 36.7503 | -1.3536
70 | 36.7548 | -1.3531
71 | 36.7585 | -1.3564
72 | 36.7531 | -1.3533
73 | 36.763 | -1.3505
74 | 36.7654 | -1.346
75 | 36.7633 | -1.3466
76 | 36.7594 | -1.3639
77 | 36.7646 | -1.3634
78 | 36.7563 | -1.3517
79 | 36.7555 | -1.3571
80 | 36.7579 | -1.35
81 | 36.7563 | -1.3508
82 | 36.7546 | -1.361
83 | 36.7566 | -1.3614
84 | 36.761 | -1.3608
85 | 36.746 | -1.3818
86 | 36.749 | -1.3815
87 | 36.7471 | -1.3571
88 | 36.7667 | -1.3805
89 | 36.7733 | -1.3796
90 | 36.7673 | -1.3638
91 | 36.7749 | -1.3786
92 | 36.7567 | -1.381
93 | 36.7568 | -1.3791
94 | 36.7552 | -1.3632
95 | 36.7505 | -1.3741
96 | 36.7635 | -1.3679
97 | 36.7624 | -1.3727
98 | 36.7682 | -1.372
99 | 36.7662 | -1.37
100 | 36.7608 | -1.3681
101 | 36.758 | -1.3421
102 | 36.7616 | -1.359
103 | 36.7682 | -1.3763
104 | 36.7635 | -1.3832
105 | 36.7612 | -1.3796
106 | 36.7645 | -1.3782
107 | 36.7603 | -1.3755
108 | 36.7579 | -1.3735
109 | 36.7587 | -1.38
110 | 36.7582 | -1.3758
111 | 36.7621 | -1.3471
112 | 36.765 | -1.3636
113 | 36.7699 | -1.38
114 | 36.7623 | -1.3607
115 | 36.7625 | -1.3609
116 | 36.7659 | -1.3649
117 | 36.7674 | -1.3682
118 | 36.7671 | -1.37
119 | 36.7692 | -1.3759
120 | 36.7582 | -1.3754
121 | 36.7579 | -1.3732
122 | 36.7586 | -1.3789
123 | 36.7612 | -1.3826
124 | 36.7411 | -1.3752
125 | 36.7463 | -1.3745
126 | 36.7463 | -1.3808
127 | 36.7555 | -1.357
128 | 36.7558 | -1.3631
129 | 36.7637 | -1.3622
130 | 36.7647 | -1.3633
131 | 36.757 | -1.3493
132 | 36.7564 | -1.3528
133 | 36.7589 | -1.3525
134 | 36.7603 | -1.3524
135 | 36.7624 | -1.3519
136 | 36.7634 | -1.3467
137 | 36.7618 | -1.3558
138 | 36.7652 | -1.3466
139 | 36.7621 | -1.3567
140 | 36.7624 | -1.3589
141 | 36.7568 | -1.3469
142 | 36.7618 | -1.3559
143 | 36.7472 | -1.381
144 | 36.7466 | -1.3745
145 | 36.7638 | -1.3621
146 | 36.7618 | -1.3618
147 | 36.7411 | -1.3742
148 | 36.7412 | -1.3773
149 | 36.754 | -1.3472
150 | 36.7586 | -1.3487